MINISTRY OF EDUCATION AND SCIENCE OF UKRAINE

NATIONAL TECHNICAL UNIVERSITY OF UKRAINE

“KYIV POLYTECHNIC INSTITUTE”

Faculty of heat power engineering

Department of nuclear power stations and thermal physics engineering

Methods engineering calculations transversely fined convective heating surfaces

HANDBOOK

for workshops

students specialties „Energy Engineering” „Nuclear Power Engineering” and „Heat Power Engineering”

Approved by the Academic Council of  NTUU “KPI“

KYIV

NTUU “KPI“

2016

Methods engineering calculations transversely fined convective heating surfaces. Handbook for workshops students specialties „Energy Engineering” „Nuclear Power Engineering” and „Heat Power Engineering” / Comp.: Eugene Pis’mennyi. – КYIV: NTUU “KPI“, 2016. – 223 p.

Griffin provided the Academic Council of NTUU "KPI"

(Protocol № 8 of 30 jule 2016)

Electronic educational editions

Methods engineering calculations transversely fined convective heating surfaces

HANDBOOK

for workshops

students specialties „Energy Engineering” „Nuclear Power Engineering” and „Heat Power Engineering”

Compiler: 		Eugene Pis’mennyi, Doctor of Technical Sciences, prof.

Responsible

editor:		Natalia Lebed, Ph.D., docent.

Reviewers:		Gennadiy Voropaev, Doctor of Technical Sciences, prof.

Viktor Klimenko, Doctor of Technical Sciences, prof.

Edited compilers

PREFACE

The purpose of the manual is to deepen students' theoretical knowledge on heat aerodynamic and hydraulic processes occurring in the heat exchangers of the cross-ribbed pipe. The authors hope that the user will be useful for senior students in mastering lectures courses "Heat and Mass Transfer" and "heat exchanger and coolant," "Boiler systems".

The manual method of calculation laid down heat transfer and drag convection heating surfaces made in the form of bundles of tubes shaybovym cross, square and spiral ribs. The method is based on the results of experimental studies conducted at the Department of nuclear power engineering and thermal physics of National Technical University of Ukraine "Kyiv Polytechnic Institute" [1, 2]. This technique, after scrutiny of the leading research and design organizations in Ukraine and Russia as the most accurate and versatile compared to other, existing today, methods of thermal and aerodynamic calculations [4-6].

The technique allows to calculate ribbed surfaces, working in conditions as clean and dust streams. The manual also includes a method of calculation of hydraulic resistance to fluid, moving in the middle of the beam pipe temperature control method of calculation of finned tubes and strength calculations, based on the recommendations of the standard method of hydraulic and thermal calculations boilers, standards of calculations for strength. Also brought practical problems.

The proposed manual includes complete set of teaching materials for analysis and design of convective surfaces constructed of transversely ribbed tubes. References required to solve engineering problems found directly in the text of the manual or in appendix.

NOMENCLATURE

A			outside heat-transfer-surface area, m2;

Ain			inside heat-transfer-surface area, m2;

Ar			heat-transfer surface-area of fins, m2;

Arct			surface of finning-carrying tubes, m2;

Ars		heat-transfer surface area of finned tube segments on outside, which is defined as difference between calculated heating surface A and surface of unfinned segments (bends and junction regions), m2;

At			tube part of heating surface not occupied by fins, m2;

CR			coefficient in similarity equation for aerodynamic resistance;

Cq			coefficient in similarity equation for heat transfer;

Cz			correction for number of tube rows in bundle in direction of gas flow;

cp			specific heat at constant pressure, J/kg K;

cv			specific heat at constant volume, J/kg K;

csq			side of square fin, m;

D = d + 2lr		finning diameter, m;

d			outside diameter of fin-carrying tube, m;

din			inside diameter of tube, m;

E			theoretical efficiency of fin;

Gf			mass flow rate of internal heat-transfer medium, kg/s;

Gg			mass flow rate of external heat-transfer medium, kg/s;

h			heat transfer coefficient, W/m2K;

hc			convective heat transfer coefficient, W/m2K;

h1rdc			reduced coefficient of heat transfer from outside (from gas), W/m2K;

h2			heat transfer coefficient from wall to internal medium, W/m2K;

i			specific enthalpy, J/kg

ifg			latent heat of evaporation, J/kg

k			thermal conductivity of heat transfer medium, W/mK;

kt			thermal conductivity of tube metal, W/mK;

kr			thermal conductivity of fin metal, W/mK;

Lc.cr.s			length of tube projection on calculated cross section of gas conduit, m;

Lrs			length of finned segment of tube, m;

Lt			total length of heated unfinned tube segments, m;

lr			fin height, m;

lre = lr + δ2/2		conventional fin height, m;

P, p			pressure of heat-transfer medium, Pa;

Q			heat transfer rate, W;

R			thermal resistance, m2K/W;

re = (D + δ2) / 2	conventional finning radius, m;

r1 = d / 2,		outside radius of tube, m;

S1			transverse spacing of tubes, m;

S2			longitudinal spacing of tubes, m;

diagonal spacing of tubes, m;

s			specific entropy, J/kg K

sr			fin spacing, m;

T, t			average temperature of internal medium in bundle, °C;

U			overallheat transfer coefficient, W/m2K;

u			velocity, m/s;

v			specific volume, m3/kg;

z			number of tubes in bundle;

ztcp			number of tubes connected in parallel;

z1			number of tubes in transverse row of bundle;

z2			number of the tube rows in bundle in direction of gasflow;

Greek symbols

α			thermal diffusivity, m2/s;

β			fin parameter, 1/m;

th			volumetric thermal expansion coefficient, 1/K

Δ			difference

ΔP			aerodynamic resistance of tube bundles in cross flow, Pa;

δr			average fin thickness, m;

δt			nominal wall thickness of tube, m;

δ1			fin thickness at base, m;

δ2			fin thickness at tip, m;

ε			contamination factor, m2K/W;

0			resistance coefficient of single tube row of bundle;

dynamic viscosity, Pas;

μr			factor taking account of fin widening towards base;

thermal efficiency factor;

density, kg/m3;

σ1 = S1 / d		relative transverse spacing of tubes;

σ2 = S2 / d		relative longitudinal spacing of tubes;

υ			kinematic viscosity, m2/s;

Ψr = Ars / At	fin coefficient (the ratio of total outside surface of finning tubes to external surface of tube not occupied by fins);

E			correction factor to theoretical efficiency of fin;

average temperature of gas in bundle, °C;

c.r			gas temperature at entrance to calculated row, °C.

Non-Dimensional Numbers

Nu	Nusselt number;

Pr	Prandtl number;

Re	Reynolds number;

Subscripts

av			average

bnd			bend

col			collector

d			based on diameter

ent			entrance

f			fluid (liquid)

evap			evaporation

g			gas

h			heated

in			inside or inlet

int			intake

max			maximum

rad			radiation

t			tube

s			saturation

sup			supply

un			unheated

v			vapor

w			wall (at wall temperature)

at inlet

at outlet

parameter with overbar means average value

Acronyms

DC			Distributing Collector

IC			Intake Collector

SC			Supply Collector

TRU			Turbo-Refrigerating Unit

WAHE		Water-to-Air Heat Exchanger

1. GENERAL STATEMENTS

  - Convective heating surfaces with circular, square or helical fins represent tube bundles or tube banks with staggered or in-line arrangement of tubes in cross flow.Bundles are fabricated from straight tubes, finned beforehand through welding by high-frequency currents or in any other manufacturing process. Geometric characteristics of finned tubes are presented in Figure 1.1.

Steps between tubes in in-line and staggered arrangements are shown in Figure 1.2.

Figure 1.1. Geometric characteristics of finned tubes: a) tube with circular fins; b) tube with square fins; and c) tube with helical fins.

Figure 1.2. Spacing characteristics of bundles of finned tubes: a) staggered arrangement; and b) in-line arrangement.

2. HEAT-TRANSFER CALCULATIONS

2.1. Basic Equations.

2.1.1. The quantity of heat, taken up by the heating surface in unit time, is found from the equation

, kW				(2.1)

where the overallheat transfer coefficient U is determined according to Section 2.2 and the average temperature difference Δt according to Section 2.7.

The calculated heating surface A is taken to be equal to the total heating surface on the outside (on the side of gas), that comprises the heating surface of fins Ar and the heating surface of tubes At, excluding the tube surface occupied by fins,

(2.2)

Ar for helical finning and circular fins is determined according to the expression

(2.3)

for square fins,

(2.4)

where Lrs is the length of the finned segments of the tubes.

Ar is calculated from the equation

(2.5)

here, Lt is the total length of the heated unfinned tube segments (bends and junction regions), which is determined from manufacturer’s drawings.

2.2. Overall Heat Transfer Coefficient

2.21. The overall heat transfer coefficient of finned tubes can be calculated with sufficient accuracy as for a plane finned wall. Here, in the case of the tube bundle washed by the flow of a pure heat-transfer medium, as well as by the combustion products of gas or black oil, use can be made of the equation

(2.6)

where.h1rdc	is the reduced heat transfer coefficient, which is determined according to Section 2.3.1;

h2	is the coefficient of heat transfer from the tube wall to the internal medium, which is determined according to Section 2.5. In calculations of the heat transfer coefficients of steaming economizers and evaporation surfaces, the thermal resistance of heat transfer to the internal medium is generally disregarded, since in these cases<<

A	is the total heating surface on the outside, which is determined from Eqs. (2.2)  (2.5);

Ain		is the inside heat transfer surface, calculated from the equation:

(2.6a)

is the thermal efficiency factor that accounts for a decrease in the heat absorption by the heating surface, resulting from its contamination and also from its nonuniform washing by gases, a partial overflowing of gases past it and the formation of stagnation regions, and it is determined according to Section 2.6;

Rt	is the thermal resistance of the tube wall: for ordinary uniform tubes with welded or rolled-on finning and for cast finned tubes,

(2.7)

- and for bimetallic finned tubes,

(2.8)

Here;	Rcont is the thermal contact resistance between the outside finned shell with the thickness δ and the thermal conductivity k and the inside smooth shell with the thickness δ and the thermal conductivity k. Rcont is determined from the reference literature or experimentally. The thermal resistance of heat transfer from the outside 1/h1rdc is generally much higher than the thermal resistance of the metal of the tube wall δt / kt , and therefore the latter can be ignored (δt / kt  ≈ 0).

2.2.2. If the bundle of finned tubes is exposed to the flow of the combustion products of solid fuels, the heat transfer coefficient is calculated from the equation

(2.9)

where h is determined according to Section 2.3.2 and the other quantities by Eq. (2.6).

2.3. Reduced Heat Transfer Coefficient h1rdc

2.3.1. Since the thickness of the radiative layer in the bundles of transversely finned tubes is small, the reduced coefficient of heat transfer from the outside is determined disregarding the inter-tube radiation.

In the case of the tube bundle exposed to a flow of a pure heat-transfer medium,

(2.10)

where hc is determined according to Section 2.4, and A, Ar and At according to Section 2.1.1.

The theoretical efficiency of the fin E for helical finning and circular fins is found as a function of the parameters β∙lr and D/d from the nomogram in Figure 2.1 or, for β∙lr ≤ 2 and D / d ≤ 3, is calculated from the equation

(2.11)

where

(2.12)

(2.13)

The conventional fin height lr is determined using the relation

(2.14)

The correction factor Eto the theoretical efficiency of the fin E, which takes account of the non-uniformity of heat transfer over the fin surface, is calculated from the equation

(2.15)

For fins with a trapezoidal cross section, the coefficientμr that takes account of the effect of the fin widening toward the root is determined from the nomogram in Figure 2.1 as a function of the parameters βlr and , (δ2 and δ1 are the fin thicknesses at the tip and root).

In determining kr, the average temperature of the fin metal is evaluated approximately using the equation

(2.16)

where  and T – are the average temperatures of the external and internal heat-transfer media.

For square fins, the theoretical efficiency of the fin E and the correction factor E are determined in exactly the same manner as for circular fins. Here, in the calculation relations it should be assumed that

(2.17)

(2.18)

2.3.2. When combustion products of solid fuels are used as a heat-transfer medium, the reduced coefficient of heat transfer from the outside of the heating surface is calculated with account for the contamination factor of the surface,

(2.19)

where the contamination factor ε, representing the thermal resistance of the layer of external deposits, is determined according to Section 2.6, and the other quantities are obtained from Eq. (2.10). As with a clean surface, E is determined from the nomogram (Figure 2.1) or from Eq. (2.11), and the correction factor E is obtained from Eq. (2.15).

Figure 2.1. Fin, correction factor μA, which takes into account fin widening towards base, and relations for theoretical efficiency of fin E.

2.4. Convective Heat Transfer Coefficient (hc)

2.4.1. The convective heat transfer coefficient depends on the velocity and physical properties of the gas flow, and on geometric characteristics of the tube bundle.

2.4.2. The design gas velocity is determined from the equation

(2.20)

At pressures close to atmospheric, ug can be determined using the equation

(2.20a)

where V is the volumetric flow rate of gases at P = 760 mm Hg and 0°C, m3/s; and F  is the minimum flow area for gas, m2.

The minimum flow area in staggered bundles can be located in the plane of transverse spacing and in the plane of diagonal spacing alike, which is determined by the value of the parameter

(2.21)

here, dcl is the conventional diameter of the finned tube

(2.22)

For φcl ≤ 2, the minimum free area is situated in the plane of transverse spacing and determined from the following equation

(2.23)

Where a and b	are the dimensions of the gas conduit in the calculated cross section, m;

Lc.cr.s	is the length of the tube projection on the calculated cross section of the gas conduit, m;

z1		is the number of tubes in the transverse row.

For φcl> 2, the minimum free area lies in the plane of diagonal spacing and is calculated from the equation

(2.24)

The minimum free area for in-line bundles is calculated from Eq. (2.23).

2.4.3. Physical properties of the external heat-transfer medium, which is usually air or flue gases, are determined at the average flow temperature in the bundle .

Table 2.1 presents the kinematic viscosity , the thermal conductivity k and the Prandtl number (Pr) for air and flue gases with the average composition at a pressure of 760 mm Hg and temperature ranging from 0 to 1000°C. The average composition of gases corresponds to the volume fractions of water vapor and carbon dioxide, which are  = 0.11 and = 0.13.

The deviation of the values of , k and Pr for flue gases with the composition different from the average one results mainly from the change in the content of water vapor. It is allowed for, correspondingly, by the corrections M, Mk and MPr to the values of av, kav and Prav, determined from Table 2.1 for the average composition,

(2.25)

(2.26)

(2.27)

Table 2.1. Physical Properties of Air and Flue Gases with the Average Composition [11].

| T, ºC | Air |  |  | Flue gases of average content |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 106 m2/s | k102 W/mК | Pr | 106 m2/s | k102 W/mК | Pr |
| 0 | 13.6 | 2.42 | 0.70 | 11.9 | 2.27 | 0.74 |
| 100 | 23.5 | 3.18 | 0.69 | 20.8 | 3.12 | 0.70 |
| 200 | 35.3 | 3.89 | 0.69 | 31.6 | 4.00 | 0.67 |
| 300 | 48.9 | 4.47 | 0.69 | 43.9 | 4.82 | 0.65 |
| 400 | 63.8 | 5.03 | 0.70 | 57.8 | 5.68 | 0.64 |
| 500 | 73.2 | 5.60 | 0.70 | 73.0 | 6.54 | 0.62 |
| 600 | 98.0 | 6.14 | 0.71 | 89.4 | 7.40 | 0.61 |
| 700 | 116 | 6.65 | 0.71 | 107.0 | 8.25 | 0.60 |
| 800 | 136 | 7.12 | 0.72 | 126.0 | 9.13 | 0.59 |
| 900 | 157 | 7.59 | 0.72 | 146.0 | 9.99 | 0.58 |
| 1000 | 179 | 8.03 | 0.72 | 167.0 | 10.87 | 0.58 |

The corrections M, Mk and MPr are determined as functions of the gas temperature and volume fraction of water vapor from Figure 2.2.

2.4.4. The convective heat transfer coefficient with a transverse flow around staggered and in-line bundles of tubes with circular, helical and square finning, referred to the total surface on the gas side, is calculated from the equation

(2.28)

where

(2.29)

(2.30)

Figure 2.2.Corrections for conversion of physical characteristics of flue gases with average composition: a) M; b) Mk; and c) MPr.

The shape parameter of the bundle X, entering into Eqs. (2.29) and (2.30), for the bundle with staggered arrangement of tubes is obtained from the equation

(2.31)

and for in-line bundles, from equation

(2.32)

The fin coefficient for circular fins is

(2.33)

and for square fins,

(2.34)

The factor Cz , which takes account of the effect of the number of transverse tube rows in the bundle on heat transfer z2 , for staggered bundles with σ1 / σ2 ≥ 2 and z2< 8 and for in-line bundles with any σ1 / σ2 and 2 ≤ z2< 8 is determined from the upper curve in Figure 2.3 or from the expression

(2.35)

for staggered bundles with σ1 / σ2< 2  and  z2< 8, it is determined from the lower curve in Figure 2.3 or from the expression

(2.36)

and for z2 ≥ 8,

(2.37)

In order to determine m and Cq as functions of the fin coefficient Ψr and the generalized arrangement parameter σ1 / σ2or σ2 , nomograms are constructed in Figures 2.4 and 2.5 for staggered bundles and in Figures. 2.6 and 2.7 for in-line bundles.

Figure 2.3. Factor Cz, taking into account effect of number of transverse tube rows in bundle on heat transfer.

Figure 2.4. Dependence of exponent m on Reynolds number in Eq. (2.28) on geometric characteristics of staggered tube bundles.

Figure 2.5. Dependence of coefficient Cq in Eq. (2.28) on geometric characteristics of staggered tube bundles.

Figure 2.6. Dependence of exponent m on Reynolds number in Eq. (2.28) on geometric characteristics of in-line tube bundles.

Figure 2.7. Dependence of coefficient Cq in Eq. (2.28) on geometric characteristics of in-line tube bundles.

2.4.5. For approximate evaluation of the heat transfer coefficients in searching for optimum geometric characteristics of the heating surface, nomograms are constructed in Figures. 2.8 - 2.17, each of which corresponds to a certain value of the Reynolds number in the range Red = 5103- 2.5104. These nomograms should be used taking into account that the Nusselt and Reynolds numbers are determined from the relations

(2.38)

(2.39)

and the fin coefficient is obtained from Eqs. (2.33) or (2.34).

It is seen from Figures. 2.8 – 2.17 that the dependences of the Nusselt numbers (the heat transfer coefficients) on the arrangement parameters have a maximum, whose position is dependent mainly on the fin coefficient Ψr , i.e., for each value of Ψr  there is an arrangement that gives a maximum value of the heat transfer coefficient.

The value of the parameter (σ1 / σ2 )max   corresponding to the maximum of the heat transfer rate with staggered arrangement can be determined using the relation

(2.40)

and the value of the parameter (σ2) corresponding to the maximum of the heat transfer rate with in-line arrangement can be determined using the relation

(2.41)

The quantity Ф in expressions (2.40) and (2.42) is a weak function of the Reynolds number (Figure (2.18),

(2.42)

At Red = 9800, Ф = 0. In practical calculations the quantity Ф for the range Red = 5000 – 25,000 can be disregarded.

Figure 2.8. Nud number as function of fin coefficient Ψr and parameter S1 / S2 for staggered tube bundles at Red = 5000.

Figure 2.9. Nud number as function of fin coefficient Ψr and parameter S1 /S2 for staggered tube bundles at Red = 10,000.

Figure 2.10. Nud number as function of fin coefficient Ψr and parameter S1 /S2 for staggered tube bundles at Red = 15,000.

Figure 2.11. Nud number as function of fin coefficient Ψr and parameter S1 /S2 for staggered tube bundles at Red = 20,000.

Figure 2.12. Nud number as function of fin coefficient Ψr and parameter S1 /S2 for staggered tube bundles at Red = 25,000.

Figure 2.13. Nud number as function of fin coefficient Ψr and parameter σ2 for in-line tube bundles at Red = 5000.

Figure 2.14. Nud number as function of fin coefficient Ψr and parameter σ2 for in-line tube bundles at Red = 10,000.

Figure 2.15. Nud number as function of fin coefficient Ψr and parameter σ2 for in-line tube bundles at Red = 15,000.

Figure 2.16. Nud number as function of fin coefficient Ψr and parameter σ2 for in-line tube bundles at Red = 20,000.

Figure 2.17. Nud number as function of fin coefficient Ψr and the parameter σ2 for in-line tube bundles at Red = 25,000.

Figure 2.18. Dependence Ф = f(Red).

2.5. Heat Transfer Coefficient from Wall to Internal Medium (h2)

2.5.1. The heat transfer coefficient in the motion of the heat-transfer medium in tubes depends on the flow regime and velocity, physical properties of the heat-transfer medium and geometric characteristics of tubes. In the elements of heat-transfer devices made in the form of bundles of finned tubes, there occurs, as a rule, the developed turbulent flow of the internal heat-transfer medium, which is usually water, vapor or (in boiling) a vapor-water mixture. The thermal resistance of heat transfer in boiling of the heat-transfer medium 1/h2 can be ignored. Therefore, in the calculation of the overall heat transfer coefficient U, the quantity h2 should be determined in the case of monophase flow in tubes.

2.5.2. For the case of longitudinal monophase turbulent flow over the inside surface of tubes at Ref = 4  103-5  106 and Prf = 0.1-2000 the heat transfer coefficient is determined from the equation

(2.43)

where

(2.44)

(2.45)

In narrower ranges Ref = 1104-1106 and Prf = 0.7 -2.0, the heat transfer coefficient h2can be determined from the simpler equation

(2.46)

In Eqs. (2.43) – (2.46),

kf	is the thermal conductivity of the internal heat-transfer medium determined from its average temperature T;

Ref=uf∙dinνf              is the Reynolds number determined based on the inside diameter of tubes, din,

the kinematic viscosity f at the average flow temperature T (f = μff) and the medium velocity

(2.47)

here, Gf  is the flow rate of the internal medium, f is its average specific volume (for water and water vapor it is determined from Tables S.1 – S.3), and f is the flow area for the passage of the heat-transfer medium, which is equal to

(2.48)

for coil surfaces, the number of tubes connected in parallel ztcp is determined by the number of tubes in the transverse row z1 and by the number of the coil starts nx ,

(2.49)

Prf =  is the Prandtl number at the average flow temperature;cp is the specific heat at constant pressure of the medium, J/kg K;

Ctem is the correction that takes account of the influence exerted by the temperature dependence of physical properties of the heat-transfer medium on the heat transfer coefficient.

For dropping liquids at μw /μf = 0.08 – 40 the correction Ctem is determined from the equation

(2.50)

here,	n = 0.11 for the heating of liquids;

n = 0.25 for the cooling of liquids;

μw is the dynamic viscosity of the medium at the average temperature of the inside surface of the tube Tw , which, with a subsequent refinement, is determined from the equation

(2.50a)

μf is the dynamic viscosity of the medium at the average flow temperature T.

For gases, the correction Ctem should be determined when they are heated, using the equation

.

2.6. Contamination Factor and Thermal Efficiency

2.6.1. When combustion products of solid fuels with loose ash are used as the external heat-transfer medium, the heat transfer coefficient is calculated with account for the contamination factors which depend on the gas velocity, the fractional composition of ash contained in the combustion products, the average temperature of gases in the bundle, geometric characteristics of the finned tubes and bundle, and on the presence of cleaning of the heating surface. The equation for the contamination factor is of the form

(2.51)

Where:ε0	is the initial contamination factor dependent on the gas velocity and the relative longitudinal spacing of tubes σ2 ;

Cd	is the correction factor taking account of the effect of the tube diameter d;

Cs	 is the correction factor taking account of the effect of the relative transverse spacing of tubes in the bundle σ1 ;

Cfr	 is the factor to account for the influence of the ash dispersity, which is determined by the residue on the screen R10; when there are no reliable data on the fractional composition of ash, it is assumed that Cfr  = 0.9;

C	 is the correction factor dependent on the fin coefficient of the tube Ψr and the angle of winding of fins on the tube γ, which is determined from the equation

(2.52)

Where:nwnd	is the number of the winding starts;

Cz	is the correction for the number of the tube rows in the bundle in the direction of the gas motion;

Δε	 is the empirical correction taking account of specific operating conditions (the type of the burned fuel, the presence of cleaning, the temperature zone, etc.).

2.6.2. In the calculation of staggered bundles, the initial contamination factor ε0and the correction factors, entering into Eq. (2.51), are determined from the graphs in Figure 2.19. The values of the correction Δε are taken from Table 2.2.

2.6.3. In the calculation of in-line bundles of tubes with transverse finning, the values of ε0 and the correction factors are determined from graphs in Figure 2.20.

The correction Δε for in-line tube bundles, operating in the gas temperature range  ≤ 400°C, is taken to be 0.0017 m2K/W.

2.6.4. When combustion products of gas and black oil are used as the external heat-transfer medium, all heating surfaces are calculated from the thermal efficiency, whose values are presented in Table 2.3.

2.6.5. When combustion products of a fuel mixture are used as the heat-transfer medium, contamination or thermal efficiency factors are taken for the more contaminating type of fuel.

Table 2.2. Values of correction factor Δε.

| No. | Type of the heating surface | Correction Δε, m2K/W |  |
| --- | --- | --- | --- |
|  |  | Products of combustion from solid fuels, which produce ash inlays, for case when surface is not cleaned | Products of combustion of other coals when performing periodic cleaning of surface |
| 1. | First stages of water economizers, single-stage economizers and other convective bundles with inlet temperature of gases ≤ 400°C | 0 | 0 |
| 2. | Second stages of water economizers, single-stage economizers with > 400°C, transition zones of once-through boilers | 0.0014 | - |

Table 2.3.Thermal efficiency factor, .

| Type of heating surface | Type of the burned fuel |  |
| --- | --- | --- |
|  | Gas | Black oil |
| Superheaters, boiler tube banks, festons and transition zones | 0.80 | 0.55 |
| "Hot" stages of economizers | 0.80 | 0.60 |
| "Cold" stages of economizers, single stage economizers, preheaters of gas-liquid type | 0.85 | 0.60 |
| The same, with inlet temperature of water equal to 100°C and lower | 0.85 | 0.45 - 0.50 |

Figure 2.19. Dependences for contamination factor of staggered bundles of transversely finned tubes.

Figure 2.20. Dependences for contamination factor of in-line bundles of transversely finned tubes.

2.6.6. In the case where bundles of tubes with transverse finning are washed by the flow of a pure heat-transfer medium, for example, air (air heaters and water-to-air heat exchangers) and the passage of the entire gas flow is ensured (a complete washing), the thermal efficiency is taken to be  = 0.95. If such surfaces are placed in air cases of complex configuration, it is necessary to assume  = 0.85, since their washing is incomplete.

2.7. Average Temperature Difference

2.7.1. The average temperature difference ΔT, i.e., the temperature difference between the heating and the heated media averaged over the entire heating surface, depends on the relative direction of motion of the media.

2.7.2. The connection scheme, in which both media all through the way move in parallel and in opposition, is called countercurrent.If the heat-exchanging media move in parallel in the same direction, this connection scheme is called co-current. The temperature difference with both schemes is determined as the logarithmic-mean temperature difference using the equation

(2.53)

where ΔTlrg is the temperature difference of the media at the end of the heating surface where it is larger, and ΔTsm is the temperature difference of the media at the end of the heating surface where it is smaller.

In the cases, where ΔTlrg /ΔTsm ≤ 1.7, the temperature difference can be determined with sufficient accuracy as the arithmetic-mean temperature difference

(2.54)

where  and T are the average temperatures of the heat-exchanging media.

2.7.3. The largest possible temperature difference is achieved with a countercurrent scheme, and the smallest with a co-current scheme. With all other connection schemes we obtain intermediate values. Therefore, if the condition is fulfilled

(2.55)

(ΔTco and ΔTcount  are the average temperature differences for the cases of co-current and countercurrent schemes, respectively), the temperature difference for any complex connection scheme can be determined from the equation

(2.56)

2.7.4. Given below are indications as to calculating the temperature difference for schemes different from purely co-current and countercurrent.

Schemes with series-mixed, parallel-mixed and crosscurrents of the heat-exchanging media are discerned (Figure 2.21).

The temperature differences for these schemes are determined from the equation

(2.57)

where ψcv	is the factor of conversion from the countercurrent scheme to a more complex one, which is determined using appropriate nomograms.

2.7.5. In the scheme with a series-mixed current, the heating surface consists of two sections connected serially with respect to both media. With transition from one section to the other the relative motion of the media changes. For the commonest schemes of a series-mixed current, presented in Figure 2.22a, the factor ψcv is determined from the nomogram in Figure 2.21. Here, the following dimensionless governing parameters should be calculated:

(2.58)

Figure 2.22. Nomogram for determining conversion factor ψcv for series-mixed current.

Figure 2.22. Schemes for calculation of average temperature difference: (a) with a series-mixed current; (b) with a parallel-mixed current; and (c) with a crosscurrent.

(2.59)

(2.60)

in these equations,

A		is the total heating surface;

Aco		is the heating surface of the co-current section;

τ1 and τ2	 are the total temperature drops in the heat-exchanging media:

- for schemes I and II (Figure 2.21a), τ1 =  -   and τ2 = T - T ;

- for scheme III, τ1 = T- T and τ2  =

(the temperature designation is given in Figure 2.21a)

2.7.6. In the scheme with a parallel-mixed current (Figure 2.21b), the heating surface consists of several sections connected serially with respect to one of the media (multipass) and in parallel with respect to the other medium (single-pass). In the calculation of the temperature difference it is immaterial whether the heating or the heated medium is single-pass.

The factor ψcv for the schemes with a parallel-mixed current is determined from the nomogram in Figure 2.23. The lines of its left half are used for the corresponding connection schemes:

curve 1, for schemes with two passes of a multipass medium, both of which are with a co-current flow relative to a single-pass medium,

curve 2, for schemes with three passes of a multipass medium, of which two are with a co-current flow and one is with a countercurrent flow relative to a single-pass medium;

curve 3, for schemes with two passes of a multipass medium, of which one (no matter the first or the second) is with a countercurrent flow relative to a single-pass medium; this scheme is also used for calculating schemes with any even number of passes with the same number of countercurrent and co-current passes;

curve 4, for schemes with three passes of a multipass medium, of which two are with a countercurrent flow and one is with a co-current flow relative to a single-pass medium;

curve 5, for schemes with two passes of a multipass medium, both of which are with a countercurrent flow relative to a single-pass medium.

The factor ψcv for schemes with an odd number of passes larger than three is taken to be equal to the half-sum of the values of ψcv  determined from curves 3 and 2 or 3 and 4, depending on what passes are larger in number, co-current or countercurrent.

Figure 2.23. Nomogram for determining conversion factor ψcv for parallel-mixed current: 1 -both passes of multipass medium are co-current; 2- three passes of multipass medium, of which two are co-current and one is countercurrent; 3- two passes of multipass medium, of which one is countercurrent and another is co-current; 4- three passes of multipass medium, of which two are countercurrent and one is co-current; and 5- both passes of multipass medium are countercurrent.

For using the nomogram in Figure 2.23 it is necessary to calculate the dimensionless parameters

(2.61)

(2.62)

where Tand 	are the initial temperatures of the heating and the heated medium, respectively;

τlrg		is the total temperature drop in the medium where it is larger;

and τsm		 is the total temperature drop in the medium where it is smaller.

2.7.7. In a crosscurrent scheme, the directions of flows of both media intercross. The average temperature difference for the crosscurrent depends mainly on the number of passes and the general relative direction of flows of the media (a co-current flow or a countercurrent flow). Crosscurrent schemes with a different number of passes are shown in Figure 2.21c.

The factor ψcv is determined from the nomogram of Figure 2.24. The lines of its left half are used for a different number of passes:

curve 1, for a onefold crosscurrent;

curve 2, for a twofold crosscurrent;

curve 3, for a threefold crosscurrent; and

curve 4, for a fourfold crosscurrent.

For using the nomogram, the same dimensionless parameters are calculated beforehand as those for a parallel-mixed current,

Figure 2.23. Nomogram for determining the conversion factor ψcv for a parallel-mixed current: 1, both passes of a multipass medium are co-current; 2, three passes of a multipass medium, of which two are co-current and one is countercurrent; 3, two passes of a multipass medium, of which one is countercurrent and the other is co-current; 4, three passes of a multipass medium, of which two are countercurrent and one is co-current; 5, both passes of a multipass medium are countercurrent

Figure 2.24. Nomogram for determining conversion factor ψcv for crosscurrent:1- one-fold crossing;2- two-fold crossing;3- three-fold crossing; and 4- four-fold crossing.

2.7.8. If the bundle of finned tubes represents a steaming economizer with the steam quality at the exit x ≤ 30%, sufficient accuracy of determining the average temperature difference is provided using, as the final temperature of the heated medium, the conventional temperature

Tcl=Tsl					(2.63)

where Tcl	 is the final temperature of the heated medium;

Tsl	 is the saturation temperature.

3. CALCULATION OF AERODYNAMIC RESISTANCE

3.1.The aerodynamic resistance of the bundles of finned tubes in crossflow

The aerodynamic resistance of the bundles of finned tubes in crossflow is determined from the equation [13, 14]:

∆P=Cop∙ςo∙z2∙ρg∙ug22, [Pa]                                          (3.1)

where Cop is the correction factor taking account of real operating conditions of the heat transfer surface, and it is taken to be Cop = 1.1; and ζ0 is the resistance coefficient referred to a single transverse row of tubes.

3.1.1. The resistance coefficient ζ0 is dependent on geometric characteristics of the bundle of finned tubes and the Reynolds number   and is determined in the range Reeq = 5103 - 6  104 for both staggered and in-line bundles from the equation

(3.2)

With staggered arrangement of tubes in the bundle, the exponent n and the coefficient Cr in Eq. (3.2) are defined by the expressions

(3.3)

(3.4)

Nomograms are constructed (Figures. 3.1 and 3.2) for determining n and Cr using Eqs. (3.3) and (3.4).

In the case of in-line arrangement of tubes, n and Cr should be determined using the following relations:

for ≤ 2,1:

(3.5)

(3.6)

and for > 2,1:

n=0					 (3.7)

(3.8)

Nomograms are constructed (Figures. 3.3 and 3.4) for determining n and Cr using Eqs. (3.5) – (3.8).

The quantity , entering into Eqs. (3.5) – (3.8), is called the reduced length of the developed surface and is defined by the expression

(3.9)

In the calculation of the resistance coefficient ζ0, the characteristic dimension in the Reynolds number Reeq is taken to be the equivalent diameter of the most contracted cross section of the bundle, which for in-line bundles and for staggered bundles with φcl ≤ 2 (φcl is determined in Section 2.4.2) is

(3.10)

and for staggered bundles with φcl> 2 is

(3.11)

where deq is determined from Eq. (3.10).

For square fins, in determining from Eq. (3.9) and deq from Eq. (3.10) it should be assumed that

(3.12)

Depending on the arrangement of finned tubes in the bundle, the correction factor taking account of the small number of rows of the bundle C is calculated using the following relations:

for staggered arrangement and z2 < 6,

(3.13)

for in-line arrangement and z2 < 6,

(3.14)

and for any arrangement of tubes and z2 ≥ 6,

(3.15)

The flow velocity in Eqs. (3.1) and (3.2) is determined according to Section 2.4.2.

Physical properties of the external heat-transfer medium are determined following the recommendations given in Section 2.4.3.

Nomograms are constructed in Figures. 3.5 – 3.14 for approximate evaluation of the resistance coefficient ζ0 during the search for optimum geometric characteristics of the heating surface.

Figure 3.1. Nomogram for determining exponent n in Eq. (3.2) for calculating resistance coefficient ζ0 of staggered bundles of finned tubes.

Figure 3.2. Nomogram for determining coefficientCr in Eq. (3.2) for calculating resistance coefficient ζ0 of staggered bundles of finned tubes.

Figure 3.3. Nomogram for determining exponent n in Eq. (3.2) for calculating resistance coefficient ζ0 of in-line bundle of finned tubes with S1 / S2 ≤ 2.1.

Figure 3.4. Nomogram for determining coefficient Cr in Eq. (3.2) for calculating resistance coefficient ζ0 of in-line bundles of finned tubes: (a)S1 /S2 ≤ 2.1; and (b)S1 /S2> 2.1.

Figure 3.5. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for staggered bundles of finned tubes at Reeq = 5000.

Figure 3.6. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for staggered bundles of finned tubes at Reeq = 10,000.

Figure 3.7. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for staggered bundles of finned tubes at Reeq = 15,000.

Figure 3.8. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for staggered bundles of finned tubes at Reeq = 20 000.

Figure 3.9. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for staggered bundles of finned tubes at Reeq = 25,000.

Figure 3.10. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for in-line bundles of finned tubes at Reeq = 5000.

Figure 3.11. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / For in-line bundles of finned tubes at Reeq = 10,000.

Figure 3.12. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2and reduced length of developed surface Atotal / F for in-line bundles of finned tubes at Reeq = 15,000.

Figure 3.13. Resistance coefficient ζ0 in Eq. (3.2) asfunction of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for in-line bundles of finned tubes at Reeq = 20,000.

Figure 3.14. Resistance coefficient ζ0 in Eq. (3.2) as function of arrangement parameter S1 / S2 and reduced length of developed surface Atotal / F for in-line bundles of finned tubes at Reeq = 25,000.

4. CALCULATION OF HYDRAULIC RESISTANCE

4.1. Hydraulic calculation of the tube elements

For the hydraulic calculation of the tube elements, use is made of the following quantities characterizing the flow of the heat-transfer medium [8-10]:

- the mass flux of the medium, kg/m2s,

(4.1)

- the linear velocity of the medium, m/s,

(4.2)

- the Reynolds number

(4.3)

- and the vapor quality of the medium

x=i-isl'ifg			                    	  (4.4)

In Eqs. (4.1) – (4.4),

Gf		is the flow rate of the internal medium, kg/s;

f	is the area of the internal cross section for the passage of the heat-transfer medium; in the calculation of the average velocity of the medium in tubes of the element, f is determined according to Section 2.5.2;

f	is the specific volume of the medium, m3/kg, determined in the calculation of local resistances that are concentrated near the inlet to the tube element or the outlet from it, respectively, from the temperatures of the medium at the inlet T or outlet T; for all other resistances it is determined from the average temperature of the medium in the tube element T;

f	is the kinematic viscosity of the medium determined from its average temperature;

ifg		is the latent heat of evaporation, kJ/kg;

isl'	is the enthalpy of the liquid phase of the internal medium on the saturation line, kJ/kg;

i	is the enthalpy of the medium in the calculated cross section or the average enthalpy in the segment (depending on what x should be determined – that in the calculation cross section or that average in the segment), kJ/kg.

4.2. Total hydraulic resistance of the tube element

The total hydraulic resistance of the tube element is expressed by the equation [9]:

(4.5)

where ΔPfr	is the hydraulic friction resistance, Pa, which is determined according to Section 4.4;

ΣΔPloc	is the pressure losses at local resistances, Pa, which are determined according to Section 4.5;

And	is the overall pressure loss in the element collectors referred to the tube with the mean flow rate of the medium, Pa, which is determined according to Section 4.6.4.

4.3. Hydraulic friction resistance and local resistances of the heat transfer surfaces,

The hydraulic friction resistance and local resistances of the heat transfer surfaces in which a phase transition occurs, for example, of evaporation surfaces and steaming economizers, are calculated separately for the segments with monophase and two-phase flows – the economizer (Lec) and the evaporation (Lev) segments, respectively. The length of each of these segments is determined from the following equations:

(4.6)

(4.7)

Where:

Ltotal – is the total length of tubes (coils) of the element from the supply collector to the intake collector, m;

Lun – is the length of unheated tube segments, m;

Lh = Lrs + Lt – is the average length of the heated tube segments, m;

h – is the enthalpy of the medium at the entrance to the element, kJ/kg;

h – is the enthalpy of the liquid phase on the saturation line, kJ/kg;

and  is the average increment of the enthalpy of the medium in the considered element, kJ/kg.

4.4. Friction Resistance

4.4.1. The friction resistance in the motion of a monophase liquid in tubes is calculated using Equation (4.8):

(4.8)

where ζfr – 	is the coefficient of hydraulic friction resistance, which is determined according to Section 4.4.2;

L – 	is the length of the calculated tube segment that is taken to be L = Ltotal in the calculation of surfaces with a monophase flow and L = Lec in the calculation of surfaces in which a phase transition occurs;

ρf – 	is the density of the medium, kg/m3, determined from the average temperature and the average pressure of the medium;

uf – 	is the linear velocity of the medium, m/s, which is determined according to Section 4.1 or Section 2.5.2.

4.4.2. The coefficient of hydraulic friction resistance ζfr is a function of the Reynolds number Ref (Section 4.1) and the relative roughness of tubes  / din.

The absolute roughness of tubes  for various materials of which tubes are made is determined according to Table 4.1.

Table 4.1. Absolute tube roughness,.

| Material | , [m] |
| --- | --- |
| Carbon and alloyed (perlite) steels | 8.010-5 |
| Austenitic steels | 1.010-5 |
| Aluminum | 1.510-5 |

The most characteristic feature of engineering heat-transfer devices, made in the form of coil tube elements, is the developed turbulent flow of the internal medium. Therefore, the values of the friction factor ζfr for Ref ≥ 560 din /  (in the self-similar region) can be calculated from the equation

(4.9)

In the cases where the self-similar flow is not reached (for example, when water moves in small-diameter tubes with Tf < 150°C and uf ≤ 0.3 m/s), it is expedient to determine the friction factor from Figure 4.1.

4.4.3. When a two-phase liquid moves in tubes and the vapor quality of the vapor-liquid mixture varies along the length of the segment, the friction resistance is obtained from the equation

(4.10)

where ζfr – is the friction factor of a monophase flow, determined according to Section 4.4.2 for a flow of the same amount of liquid;

(uρ)f – is the mass velocity of liquid, kg/m2s), determined according to Section 4.1;

ρ – is the liquid density on the saturation line, kg/m3;

ρ – is the dry vapor density on the saturation line, kg/m3;

– is the average vapor quality in the evaporation segment, determined according to Section 4.1 using Eq. (4.4); in the case where the considered section coincides with that where evaporation begins,  can be determined using the equation

(4.11)

here, h – is the enthalpy of the medium at the outlet from the element;

tw.ph – is the coefficient, determined from Eq. (4.12) and Figure 4.2,

(4.12)

where x and x – are the vapor qualities of the medium at the inlet to the considered segment and at the outlet from it, which are determined according to Section 4.1;

and  and  – are the quantities determined according to Figure 4.2 from the initial x and final x vapor qualities in the considered segment.

Figure 4.1. Friction factor in rough tubes.

Figure 4.2. Values of coefficient tw.ph in Eq. (4.12): (a) – for x< 0.7 and uf < 10 m/s; and (b) – for uf > 10 m/s.

4.5. The local resistances in the tube elements

The local resistances in the tube elements are, as a rule, composed of local resistances of the entrance to tubes from collectors and of the exit from tubes to collectors, and of local resistances of the flow turns (the tube bends).

4.5.1. The local resistances in the motion of a monophase liquid in tubes are determined from the equation

(4.13)

where ζloc – is the local resistance coefficient, determined according to the type of the local resistance using the data in Section 4.5.2, 4.5.3 and 4.5.4;

ρf – is the density of the medium, kg/m3, determined according to Section 4.1 in the same manner as is the specific volume f ;

uf – is the flow velocity, m/s, to which we refer the local resistances.

4.5.2. The average resistance coefficients of the entrance to the tube ζent are determined from Table 4.2 or Figure 4.3.

Table 4.2. Average resistance coefficients of tube entrance, ζent.

| Type of tube entrance | Resistance coefficient |  |
| --- | --- | --- |
|  | 0.1 | 0.1 |
| To heated tube from distributing collector with end or side supply of medium (Figure 4.3, case 2) | 0.5 | 0.7 |
| To heated tube from distributing collector with radial supply of medium and with number of outlet tubes n ≤ 30 per one inlet tube (Figure 4.3, case 1) | 0.5 | 0.7 |
| To heated tube from distributing collector with radial supply of medium and with number of outlet tubes n> 30 per one inlet tube (Figure 4.3, case 1) | 0.6 | 0.8 |
| To outlet tube of intake collector with end or side outlet of medium (Figure 4.3, case 3) | 0.4 | 0.4 |
| To outlet tube of intake collector with distributed radial outlets of medium (in active zone) (Figure 4.3, case 4) | 0.5 | 0.5 |

4.5.3. The average resistance coefficients of the exit from the tube ζex , related to the velocity in it, are determined from Table 4.3.

Table 4.3. Average resistance coefficients of tube exit, ζex.

| Type of tube exit | ex |
| --- | --- |
| To collector with end inlet of medium | 0.8 |
| To collector with radial inlet of medium in active zone | 1.1 |
| To collector with side inlet of medium | 1.3 |

Figure 4.3. Diagrams for calculation of resistance coefficients of tube entrance and exit:1-distribution collector with radial inlet; 2-distribution collector with side inlet; 3 - intake collector with end outlet; and 4-intake collector with distributed radial outlets in active zone.

Figure 4.4. Nomograms for determining resistance coefficients of bends (ζbnd = ζnC ); C is correction coefficient on roughnesses that are smaller than those adopted on main area of nomogram: (a); and (b)

4.5.4. The resistance coefficients of turns (bends) ζbnd are assumed using Figure 4.4 or Table 4.4 depending on the relative radius of the bend R/din and the angle of turn φ.

Table 4.4. Resistance coefficients of turns (bends), ζbnd.

| Angle of turn φ | Radius of the bend |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 |
| 60º | 0.32 | 0.25 | 0.21 | 0.18 | 0.16 | 0.15 |
| 90º | 0.41 | 0.34 | 0.3 | 0.24 | 0.22 | 0.2 |
| 120º | 0.5 | 0.4 | 0.34 | 0.27 | 0.24 | 0.22 |
| 180º | 0.6 | 0.48 | 0.4 | 0.32 | 0.28 | 0.26 |

4.5.5. The local resistances in the motion of a two-phase liquid in tubes are determined from the equation

(4.14)

where Σζ– is the sum of conventional local resistance coefficients, determined according to Section 4.5.6 – 4.5.8. The other quantities in Eq. (4.14) are determined in the same manner as in Section 4.4.3.

4.5.6. The conventional resistance coefficients of the entrance of a two-phase flow ζ to vertical and inclined tubes from collectors are assumed using Table 4.5 depending on the relative tube height Lh / din.

The conventional resistance coefficients of the mixture entrance to horizontal tubes are taken to be equal to the resistance coefficients for a uniphase medium (Section 4.5.2).

Table 4.5. Resistance coefficients of two-phase-flow entrance, ζ

| Arrangement of tubes | Relative tube height |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10 | 20 | 50 | 80 | 10 | 20 | 50 | 80 |
|  | P 6.0 МPа |  |  |  | P6.0 МPа |  |  |  |
| Vertical | 0.3 | 0.5 | 0.8 | 1.0 | 0.6 | 0.9 | 1.1 | 1.2 |
| At an angle, with progression to a vertical | 0.5 | 1.1 | 1.7 | 2.2 | 1.0 | 1.2 | 1.4 | 1.5 |

4.5.7. The conventional resistance coefficients of the exit of a two-phase medium from the tube to the enclosure ζ, including to collectors with distributed supply and withdrawal, are taken to be

ζ = 1.2

4.5.8. The resistance coefficients of turns (bends) ζ in a two-phase flow depend on the arrangement and length of the tube segments behind the turn L.

For the mass velocities of the medium (uρ)f ≤ 1200 kg/m2s, on the average, the following values of ζ are assumed:

| - a horizontal or small (L/din ≤ 10) vertical or inclined segment (for example, with a turn ahead of the entrance to the collector) |  |
| --- | --- |
| - an inclined segment (L/din> 10) with the angle of elevation not larger than 15° |  |
| - a vertical or inclined segment with the angle of elevation larger than 15° and L/din> 10 |  |
| - a lowering, vertical or inclined segment (the angle of turn is larger than 90°) with L/din> 10 |  |

ζbnd - is the resistance coefficient of a given turn with the motion of a monophase medium (Section 4.5.4).

With the mass velocities (uρ)f> 1200 kg/m2s for all schemes the values of the resistance coefficients of turns ζ are taken as for a monophase medium (Section 4.5.4),

.

4.6. Pressure Variation in Collectors [9]

4.6.1. In convective heat-transfer surfaces, horizontal collectors are generally used that supply the medium through tubes (Distributing Collector (DC) or Supply Collector(SC)) and collect it from tubes (Intake Collector (IC)). A part of the collector, into which the medium is fed or from which it is withdrawn, is called the active part.

According to the arrangement of inlet and outlet tubes, collectors with “radial” and “end” supply or withdrawal of the medium are distinguished. The radial supply (withdrawal) can be carried out both within and beyond the active zone. In the first case, the inlets (the outlets) are placed uniformly lengthwise and such a collector is called a collector with uniform supply or withdrawal. A nonuniform positioning of the radial inlets or outlets is also possible. The radial supply (withdrawal) of the medium beyond the active zone is called lateral or angular.

4.6.2. The static pressure varies along the length of collectors as a result of the change in the medium velocities and of nonrecoverable losses due to friction and at local resistances. The variation in the static pressure along the length of the collector influences the pressure difference between the inlet and outlet cross sections of the attached tubes, causing a nonuniform distribution of the medium between them (a hydraulic maldistribution). This should be taken into account especially with a unidirectional supply or withdrawal of the medium. The variation in static pressure along the length of collectors can be disregarded when the medium is uniformly supplied to or withdrawn from them by tubes, located in no less than three cross sections of its active part, and when the cross-sectional area of the collector is larger than the total cross-sectional area of all attached inlet (outlet) tubes. For the evaporation and economizer surfaces, the pressure drop in collectors may be not checked when only the second condition is fulfilled.

The total hydraulic resistance of the tube element is determined taking into account the static pressure losses in the collector segments from the entrance of the medium (the exit for IC) to the tube with the mean flow rate of the medium.

4.6.3. The maximum variation in the static pressure along the length of a horizontally positioned collector is determined from the equation

,					(4.15)

where:

ufmax –	is the maximum velocity of the medium in the collector (at the entrance to SC and at the exit from IC);

ρf  –	 is the medium density in the collector;

B – 	is the coefficient taking into account losses in the collector, which is assumed according to Table 4.6.

The values of B, indicated in Table 4.6 for a radial supply of the medium, refer to inlet tubes whose axes are at angles between 60° and 120° to the axes of heated tubes. With other angles (especially with those close to 180°C), the values of the coefficients B can be markedly different from those given in Table 4.6. The hydraulic maldistribution with angles larger than 120° can noticeably increase, therefore inlet tubes should not be positioned at such angles to heated tubes.

Table 4.6. Values of coefficient B.

| Type of the collector | B |
| --- | --- |
| For Intake Collectors (ICs): |  |
| with radial outlet in center of active part | 1.8 |
| with end outlet | 2.0 |
| For DistributingCollectors (DCs): |  |
| with radial inlet in center of active part and fcol /finl = 1.0 | 1.6 |
| with radial inlet in center of active part and fcol /finl = 1.5 | 2.0 |
| with end inlet with full cross section andfcol = finl | 0.8 |
| with end inlet with not full cross section and fcol>finl | 2(– 0.6) |
| with angular inler (beyond active zone) | 1.0 |

In Table 4.6,

fcol –		 is the area of the internal cross section of the collector, and

finl – 	is the overall cross-sectional area of all tubes feeding the medium to the supply collector.

4.6.4. The total static pressure loss in the horizontal supply and intake collectors of the element based on the tube with the mean flow rate of the medium ΔPcol, is determined according to the scheme of the medium motion in the calculated element (Figure 4.5) from the following equations:

- for П, Z, 2П, ГР, ПР, ZП , ПZ and ТР schemes of the medium motion in the tube elements,

(4.16)

- for a unidirectional end supply and a uniform radial withdrawal (n ≥ 3),

(4.17)

- for a distributed radial supply (n ≥ 3) and a unidirectional end withdrawal,

(4.18)

- for distributed coaxial supply (n ≥ 3) and withdrawal (n ≥ 3),

;						(4.19)

and for a concentrated supply in the center of the active part of the collector and a uniformly distributed withdrawal (n ≥ 3),

(4.20)

In Eqs. (4.16) – (4.20), ΔP and ΔP are the maximum variations in the static pressure in the supply and intake collectors of the element, which are determined according to Section 4.6.3.

Figure 4.5. Schemes of medium flow in tube elements.

4.6.5. The difference of total pressure drops in the supply and intake collectors of the calculated element for cross sections with a 	maldistributed tube and the mean flow rate of the medium δPcol is determined according to the scheme of the medium motion in the element (Figure 4.5) and the value of the ratio ΔP / ΔP using the following equations:

- for the П	scheme,

for  1;			(4.21)

for  1;			(4.22)

- for the ПZ scheme,

for  4;		(4.23)

for  4;		(4.24)

- and for the Z, ГР, ПР, ZП and ТР schemes,

(4.25)

In Eqs. (4.21) – (4.25), ΔP and ΔP are the maximum variations in the static pressure in the supply and intake collectors of the element, which are determined according to Section 4.6.3.

5. CALCULATION OF TEMPERATURE MODE OF FINNED TUBES

5.1. Order to evaluate the reliability and perform the strength design for transversely finned tubes

In order to evaluate the reliability and perform the strength design for transversely finned tubes, operating under the conditions of high heat loads and high temperatures of the heat-exchanging media, the calculation of their temperature mode is done that lies in determining [13]:

- the temperatures of the fin base and tip;

- the mean integral temperature of the fin;

- and the temperature of the inside surface of the tube.

The temperature mode is calculated at the places of the heat transfer surfaces, where the specific heat absorption and the temperature of the heated medium are high, and the hydraulic maldistribution is large. The combination of these factors can also result in large values of the above temperatures (Figure 5.1).

5.2. Temperature of the fin base

The temperature of the fin base is determined from the expression

T1=Tc.cr.s+∆Tt+βd∙λ∙qmax103Θk∙δtkt∙21+βd+1h2		              (5.1)

where Tc.cr.s – is the average temperature of the internal (heated) medium in the calculated cross section of the considered surface element, determined according to Section 5.2.1;

ΔTt – is the excess of the temperature of the internal medium in the maldistributed tube over the average temperature in the calculated cross section, determined according to Section 5.2.3;

βd = d/din  is the ratio of the outside and inside diameters of the finning-carrying tube;

𝜆 – is the coefficient of heat distribution, taken to be 𝜆 = 1;

δt – is the wall thickness of the finning-carrying tube;

kt – is the thermal conductivity of the metal of the wall of the finning-carrying tube dependent on the material of the wall and its average temperature Tw; for determining kt it is possible to assume, with a subsequent refinement,

;				(5.2)

h2 – is the coefficient of heat transfer from the wall to the internal medium, determined according to Section 5.2.5;

Θk – is the ratio of the temperature difference between the outside and the inside surfaces of the finning-carrying tube in the cross section, passing through the middle of the fin, to the tube-length-average value of this difference; it is calculated from the equation

(5.3)

and qmax – is the heat flux at the point of the maximum heat absorption of the most loaded tube, kW/m2, determined according to Section 5.2.4.

5.2.1. The average temperature of the internal medium in the calculated cross section of the considered surface element Tc.cr.s for evaporation heat transfer surfaces is taken to be equal to the saturation temperature. For other types of surfaces, it is determined from the medium enthalpy in the calculated cross section

(5.4)

where h – is the medium enthalpy at the entrance to the element, kJ/kg;

Δhx – is the average increment of the medium enthalpy in the tube element up to the calculated cross section, evaluated according to Section 5.2.2.

In this case, by the element is meant a tubular heating surface situated between two collectors (Figure 5.2). If the heat transfer surface does not have intermediate mixing collectors, the calculated element is the entire heat transfer surface considered.

5.2.2. The average increment of the medium enthalpy from the beginning of the element up to the calculated cross section is

, kJ/kg					(5.5)

where ηwd – is the coefficient of nonuniformity of the heat transfer rate of the element across the width of the gas conduit; for the gas temperature at the entrance to the convection bundle  ≤ 900°C, it is possible to assume ηwd = 1,0 irrespective of the element position across the width of the gas conduit;

Gel – is the flow rate of the internal medium in the element, kg/s;

Qseg – is the heat transfer rate of the element segment up to the calculated cross section, kW, which is determined disregarding the intertube radiation because of the small thickness of the radiative layer in the bundles of finned tube,

(5.6)

here, Qrad – is the heat transfer rate of the calculated segment by radiation from the gas volume in front of the bundle, kW, determined according to Section 5.2.2.1; and Qc is the heat transfer rate of the calculated segment by convection, kW, determined according to Section 5.2.2.2.

5.2.2.1. The heat transfer arte of the calculated segment by radiation from the gas volume in front of the bundle is

(5.7)

Figure 5.1. Schematic of disposition of calculation points in determining characteristic temperatures of finned tube.

Figure 5.2. Sample of two-stage convective heat-transfer surface with complex countercurrent-cocurrent scheme of medium flow and intermediate mixing collector.

Here,

Arad – is the radiation-absorbing surface of the calculated segment

(5.8)

Fi ar  – is the area of the surface, passing through the axes of tubes of the i-th row of the bundles;

xi row – is the angular coefficient of the i-th row of the bundle, determined from Figure 5.3 for the 1st row and from Figure 5.4 for the other tube rows;

n = z2seg – is the number of the tube rows in the direction of the gas motion within the calculated segment;

qrad – is the specific heat absorption of the calculated segment by radiation from the preceding gas volume

; kW/m2				(5.9)

in Eq. (5.9),

T – is the gas temperature in the preceding gas volume

;						(5.10)

acont – is the emissivity factor of the contaminated tube walls, taken to be acont = 0.8;

a – is the emissivity factor of gases in the preceding gas volume, defined by the expression

,						(5.11)

where P = Pg – is the pressure in the gas conduit, MPa;

s – is the effective thickness of the radiative layer of the gas volume, bounded on all sides, m, which is determined from the equation

,                                                             (5.12)

in which

Vb.sp – is the volume of the space in front of the bundle, m3;

Fb.sp  – is the area of surfaces, bounding the preceding volume, m2;

K – is the radiant absorptance of the gas medium, 1/m MPa;

in the case of a dust-laden gas flow over the bundle of finned tubes,

(5.13)

here, rtot = r + r is the total volume fraction of triatomic gases in the flow of the external heat-transfer medium; r is the volume fraction of water vapor; Kg is the radiant absorptance of triatomic gases,

(5.14)

ash – is the concentration of ash particles in the gas flow;

Kash – is the radiant absorptance of ash particles,

(5.15)

the coefficient Bash is chosen from Table 5.1 depending on combustion products of which fuel make the gas flow, moving in the gas conduit.

Figure 5.3. Angular coefficient of row of tube bundle first from radiation source.

Figure 5.4. Angular coefficients of row of tube bundle second from radiation source and of subsequent rows.

Table 5.1.Values of empirical coefficient, Bash.

| Fuel | Bash |
| --- | --- |
| Anthracite Black and lean coals Brown coals Shales Peat | 1.0 0.80 0.75 0.75 0.65 |

For a dust-free gas flow, the second term in Eq. (5.13) is taken to be zero.

Ts.cont – is the segment-average temperature of the contaminated walls of tubes of the heating surface, determined from the value of Qseg , assumed beforehand, using the equation

(5.16)

the obtained value of Ts.cont is refined if the values of Qseg , assumed beforehand and found from Eq. (5.6), differ by more than 5%.

In Eq. (5.16),

seg is the average temperature of the heated medium in the calculated segment, computed from the inlet Tand outlet Ttemperatures of the medium,

(5.17)

since the inlet cross sections of the calculated segment and considered element coincide, then,

the outlet cross section of the segment corresponds with the calculated cross section of the considered element, therefore the temperature at the outlet from the calculated segment T is simultaneously the average temperature in the calculated cross section of the element

T – is determined according to Eqs. (5.4) and (5.5) using the value of Qseg , assumed beforehand in expression (5.16), and, if needed, is refined together with Ts.cont ;

As.tot – is the total heating surface of the segment, calculated from the number of tubes zseg within the segment according to Eqs. (2.2) – (2.5);

εseg – is the contamination factor of tubes in the segment, m2K/W, determined according to Section 2.6; if the decrease in the heat absorption of the surface as a result of its contamination is taken into account by the thermal efficiency , εseg can be approximately evaluated from the equation

(5.18)

where  – is the average gas temperature in the calculated segment, calculated from the inlet  and the outlet  gas temperatures in the segment

(5.19)

the gas temperature at the inlet to the calculated segment is taken to be the same as at the inlet to the considered element (the bundle)

the gas temperature at the outlet from the calculated segment  is approximately evaluated from the equation

(5.20)

in which  is the gas temperature at the outlet from the considered bundle, z2 is the number of tube rows in the bundle in the direction of the gas motion, z2seg is the number of tube rows in the direction of the gas motion within the calculated segment, and  is determined from Eq. (5.17).

5.2.2.2. The heat absorption of the calculated segment by convection is determined from the expression

, kW				(5.21)

in which hc is the convective heat transfer coefficient for the bundle on the whole, determined according to Section 2.44;

As.tot – is the total heating surface of the segment (Section 5.2.2.1);

– is the average gas temperature in the calculated segment, determined from Eq. (5.19);

and ts.cont  – is the average temperature of the contaminated wall in the calculated segment

(5.22)

where Ts.cont is determined from Eq. (5.16).

5.2.3. The excess of the medium temperature in the maldistributed tube over the average medium temperature in the calculated cross section of the considered element is defined by the expression

(5.23)

here, Tc.cr.s  is the average temperature of the internal medium in the calculated cross section of the element tubes, determined according to Section 5.2.1;

and Tmax is the medium temperature in the calculated cross section of the most heated (maldistributed) tube of the element, determined from the enthalpy hmax, which is equal to

(5.24)

in Eq. (5.24),

hc.cr.s – is the medium enthalpy corresponding to the average temperature in the calculated cross section of the element tubes Tc.cr.s, determined according to Section 5.2.1;

Δhx – is the average increment of the medium enthalpy in the element up to the calculated cross section, determined according to Section 5.2.2;

ηstr – is the coefficient of structural nonequivalence of coils (the ratio of the heated surface of the maldistributed tube to the surface of the middle tube of the element, determined from geometric characteristics of tubes of the considered element;

ηt – is the coefficient of nonuniformity of heat absorption of the maldistributed tubes of the element based on the average heat absorption of the element;

for the gas temperature at the inlet to the bundle ’  ≤ 900°C it is taken to be

ηt  = 1.15,

irrespective of the position of the element over the width of the gas conduit;

ρh – is the coefficient of hydraulic maldistribution of the flow rate of the medium in the element tubes, which represents the ratio of the flow rates of the medium in the maldistributed tube to the mean flow rate of the medium in the element tubes; it is determined from the following equations:

- for steam superheaters in the general case,

(5.25)

- for steam superheaters with uniformly distributed supply and withdrawal of the medium with the same spatial arrangement of the inlet and outlet collectors,

(5.26)

- for economizer surfaces, the values of ρh  can be approximately taken to be ρh ≈ 0.8 for steaming economizers and ρh≈ 0.9 for nonsteaming economizers.

In Eqs. (5.25) – (5.26),

δPcol – is the difference of total pressure drops in the inlet and outlet collectors of the calculated element for cross sections with the maldistributed tube and the mean flow rate of the medium, determined according to Section 4.6.5;

ΔPel – is the total hydraulic resistance of the calculated element, determined according to the recommendations in Section 4.2;

ηh – is the coefficient of hydraulic nonuniformity, representing the ratio of the total coefficient of hydraulic resistance of the maldistributed tube zt to the total coefficient of hydraulic resistance of the calculated element zel ,

(5.27)

where ζfr and ζlocare determined according to the recommendations in Sections 4.4 and 4.5;

– is the average specific volume of the medium in the element, determined from the average temperature and pressure of the medium in the calculated element;

t – is the average specific volume of the medium in the maldistributed tube, determined from the average temperature of the medium in the maldistributed tube Tt

(5.28)

here, T’  – is the medium temperature at the inlet to the element;

T – is the medium temperature at the outlet from the maldistributed tube, which is determined with a subsequent refinement from the appropriate value of the enthalpy

(5.29)

obtained from the preliminarily assumed value of ρh and the average increment of the medium enthalpy in the element;

the value of  is taken to be unity for ≤ 160 kJ/kg and medium pressures Pf  ≤ 10 MPa, and also for  ≤ 120 kJ/kg and Pf > 10 MPa.

If the inlet collector of the calculated element is intermediate and the admission of the medium into it does not provide its complete mixing, yet another term is introduced in the right-hand side of Eq. (5.24) that takes account of the thermal maldistribution in the preceding element

(5.30)

here, the subscripts “pr” refers to the element preceding the calculated one; ain.m is the coefficient taking account of the incompleteness of the medium mixing in the preceding element, which is taken to be

- ain.m = 0 with a one-sided admission of the medium into the end of the collector or with a complete mixing of the medium in the preceding element;

-ain.m = 0.5 with a two-sided admission of the medium into the ends of the supply collector, and also with a small relative number of inlet tubes, distributed along the collector ninl / nout  ≤ 0.3;

- and ain.m = 1.0 with an intermediate collector, and also with a large relative number of tubes, feeding the medium to the supply collector ninl / nout> 0.3.

5.2.4. The specific heat load at the point of maximum heat absorption of the most loaded tube is defined by the expression

(5.31)

where ηwd – is the coefficient of nonuniformity of heat absorption of the element across the width of the gas conduit, determined according to Section 5.2.2;

ηt – is the coefficient of nonuniformity of heat absorption of maldistributed tubes of the element across the width of the gas conduit, determined according to Section 5.2.3;

q0 – is the average specific heat absorption of the most heated generating tube in the calculated cross section, kW/m2,

(5.32)

In Eq. (5.32),

c.r – is the gas temperature at the entrance to the calculated row, approximately evaluated from the equation

(5.33)

where z2 up c.cr.s – is the number of tube rows in the direction of the gas motion up to the calculated cross section; the other quantities are determined as in Eq. (5.20), Section 5.2.2.1;

T c.cr.s – is the average temperature of the heated medium in the calculated cross section, determined according to Section 5.2.1;

h2 – is the coefficient of heat transfer from the wall to the internal medium, determined according to Section 5.2.5;

εseg – is the contamination factor of tubes of the calculated segment, determined according to Section 5.2.2.1;

h1 – is the coefficient of heat transfer from gases to the wall at the point of maximum heat absorption in the calculated cross section, determined from the equation

(5.34)

where cfr – is the coefficient of nonuniformity of heat absorption over the circumference of the tube, taken to be cfr = 1.3;

– is the reduced coefficient of heat transfer from the gas side based on the surface of the finning-carrying tube Acar,

(5.35)

in this equation,

(5.36)

(5.37)

hc – is the circumference-average convective heat transfer coefficient in the calculated cross section, determined according to Section 2.4.4 with account for the position of the calculated tube row over the bundle depth; here, the factor Cz in Eq. (2.28) should be determined as follows:

- for tubes of the first row, as for a three-row bundle;

- for tubes of the second row, as for a five-row bundle;

- and for tubes of the third and subsequent rows, Cz = 1;

the other quantities in Eq. (5.35) are determined according to Section 2.3.1;

hrad – is the heat transfer coefficient taking account of the heat, received through radiation from the gas volume preceding the bundle; it is allowed only for the first and the second rows of staggered bundles and for the first row of an in-line bundle and is obtained from the equation

(5.38)

in which qrad is determined from Eq. (5.9) in Section 5.2.2.1, c.r from Eq. (5.39) and Ts.cont from Eqs. (5.16) – (5.22).

φp – is the irradiance coefficient of the point with maximum heat absorption, determined depending on the bundle arrangement and the number of the tube row with the calculated cross section relative to the external radiation source as follows:

- for tubes of the first row behind the radiation source, φp = 1,

- and for tubes of the second row of a staggered bundle, it is determined from Figure 5.5.

The remaining designation in Eq. (5.32) is the same as in Eq. (5.1).

5.2.5. The coefficient of heat transfer from the wall to the internal medium α2 for nonboiling water and water vapor at pressures Pf ≤ 18 MPa, as well as for other uniphase heat-transfer media, is obtained from Eqs. (2.43) and (2.46) in Section 2.5.2. For boiling water, h2 is determined from Figure 5.6 as a function of the specific heat flux qmax  based on the inside surface of the tube,

(5.39)

here, h2 is determined by the iteration method from qmax , evaluated beforehand using Eqs. (5.31) and (5.32).

Figure 5.5. Irradiance coefficient of points with maximum specific heat absorption for tubes of staggered bundles.

Figure 5.6. Heat transfer coefficient h2 for boiling water.

5.3. Temperature at Fin Tip

(5.40)

where, T1 – is the temperature of the fin root, determined according to Section 5.2;

I0, I1, K0 and K1 are modified Bessel functions, determined from the values of the arguments βr1and βre according to Table 5.2. In the expressions for the arguments,

β – is the fin parameter (see Eq. 2.13 in Section 2.3.1);

r1 – is the outside radius of the finning-carrying tube;

re – is the conventional finning radius, determined from the following equations:

- for circular fins,

(5.41)

- and for square fins,

(5.42)

5.4. Mean Integral Temperature of Fin

(5.43)

where, T1 is determined according to Section 5.2, and E according to Section 2.3.1.

5.5. Temperature of the Inside Surface of Tube

(5.44)

the quantities, entering into Eq. (5.44), are determined according to Section 5.2.

5.6. Thickness-average temperature of the tube wall

The thickness-average temperature of the tube wall in the region of maximum heat flux is

(5.45)

the quantities, entering into Eq. (5.45), are determined in accordance with Section 5.2.

Table 5.2. Bessel functions

| r | І0(r) | І1(r) | К0(r) | К1(r) |
| --- | --- | --- | --- | --- |
| 0.0 | 1.000 |  | 0 |  |
| 0.1 | 1.003 | 2.447 | 0.050 | 9.854 |
| 0.2 | 1.010 | 1.753 | 0.101 | 4.776 |
| 0.3 | 1.023 | 1.373 | 0.152 | 3.056 |
| 0.4 | 1.040 | 1.115 | 0.204 | 2.184 |
| 0.5 | 1.064 | 0.924 | 0.258 | 1.656 |
| 0.6 | 1.092 | 0.775 | 0.314 | 1.303 |
| 0.7 | 1.126 | 0.661 | 0.372 | 1.050 |
| 0.8 | 1.166 | 0.565 | 0.433 | 0.862 |
| 0.9 | 1.213 | 0.487 | 0.497 | 0.717 |
| 1.0 | 1.266 | 0.421 | 0.565 | 0.602 |
| 1.2 | 1.394 | 0.318 | 0.715 | 0.435 |
| 1.4 | 1.553 | 0.244 | 0.886 | 0.320 |
| 1.6 | 1.750 | 0.188 | 1.085 | 0.241 |
| 1.8 | 1.989 | 0.159 | 1.317 | 0.183 |
| 2.0 | 2.279 | 0.114 | 1.591 | 0.140 |
| 2.5 | 3.289 | 0.062 | 2.517 | 0.0739 |
| 3.0 | 4.881 | 0.0347 | 3.395 | 0.0402 |
| 3.5 | 7.378 | 0.0196 | 6.206 | 0.0222 |
| 4.0 | 11.302 | 0.0112 | 9.759 | 0.0125 |
| 4.5 | 17.481 | 0.0064 | 15.389 | 0.00708 |
| 5.0 | 27.240 | 0.0037 | 24.336 | 0.00404 |

6. STRENGTH DESIGN [12]

6.1. Strength design of heat transfer surfaces

The strength design of heat transfer surfaces composed of tubes with transverse finning lies, as a rule, in determining the allowable wall thickness (δ) of the finning-carrying tube, corresponding with the operating conditions and the selected material, and in comparing it with the nominal wall thickness δt , assumed beforehand in structural characteristics in the heat transfer surface.

The design relies on such basic concepts as

- design pressure,

- design temperature,

- and allowable stress.

6.2. Design Pressure

6.2.1. The design pressure P is taken to mean the excess pressure of the working medium, on which the strength design of the given detail (the tube) is based.

The design pressure should be equal to or higher than the maximum pressure of the working medium that is possible for the given detail (the tube) under normal operating conditions. The need for the excess of the design pressure over the working pressure, as well as the magnitude of this excess, are determined with account for structural features of the heat-transfer device, parts it comes complete with (for example, safety valves), the purpose of the heat-transfer device and experience in its operation.

6.2.2. The design pressure in tubes of the heating surfaces is assumed to be equal to the pressure of the working medium at the entrance to the calculated bundle (the element).

In all cases, the design pressure should be taken to be at least 0.2 MPa.

6.3. Design Temperature

6.3.1. By the design wall temperature Tw is meant the metal temperature according to which the allowable stress is selected for the considered detail (the tube) of the heat-transfer device.

6.3.2. The temperatures on the outside T1 and inside T2 surfaces of the finned tube, the tube temperature average over the wall thickness Tw and the temperature at the fin tip t are determined in accordance with the recommendations in Section 5.

According to the design temperature of the tube wall Tw , the heat-transfer surfaces are divided into two groups – low-temperature and high-temperature.

Among the low-temperature surfaces are surfaces with the maximum temperature of the tube walls lower than the temperature of the commencement of an intense creep of the metal. Among the high-temperature surfaces are surfaces, for which the maximum temperature is higher than that indicated (Table 6.1).

Table 6.1. Clasification of heat transfer surfaces at low and high temperatures

| Steel | Low-temperature surfaces | High-temperature surfaces |
| --- | --- | --- |
| Carbon steel | 400ºС | 400ºС |
| Alloy steel with reduced content of Cr and Mo | 425ºС | 425ºС |

The ultimate temperature of the outside tube surface corresponds with the temperature of the fin root T1, determined from Eq. (5.1). Its value should not be larger than those indicated in Table 6.2,

T1  [T1 ]								(6.1)

Table 6.2. Allowable temperature of outside tube surface [T1].

| Steel grade | Carbon steel | Alloy steel with reduced content of Cr and Mo |
| --- | --- | --- |
| [T1], ºС | 450 | 550 |

For the fin metal, the ultimate temperature T3, calculated from Eq. (5.40), should not exceed the values indicated in Table 6.3,

T3  [T3]							(6.2)

Table 6.3. Allowable temperature of fin metal [T3].

| Steel grade | Carbon steel | Alloy steel with reduced content of Cr and Mo |
| --- | --- | --- |
| [T3], ºС | 500 | 570 |

6.4. Allowable Stress

6.4.1. The nominal allowable stress [σ] is taken to mean the magnitude of stress used for determining the design thickness of the tube wall on the basis of the adopted initial data and the steel grade.

6.4.2. The nominal allowable stresses [σ] for rolled or wrought steel of grades, widely employed in convective finned heating surfaces, should be assumed in accordance with Tables 6.4 – 6.6 depending on the design temperature of the tube wall Tw and the service life of the heating surface.

For values of the service life intermediate to those indicated in the tables, it is permissible to determine the allowable stresses by the linear interpolation between the nearest values with a rounding off of up to 0.5 MPa to the side of decreasing magnitudes, if the difference between these values is no more than 20% of the average value of [σ] in the considered range. In other cases, the “logarithmic” interpolation should be used.

6.5. Calculation of Allowable Wall Thickness of Finning-Carrying Tube

6.5.1. This calculation involves the following concepts:

- the design wall thickness δcalc ,

- the nominal wall thickness δt ,

- and the allowable wall thickness [δ].

6.5.2. The design wall thickness δcalc is calculated from the preset design pressure P and nominal allowable stress [σ] using the equation

(6.3)

where d is the inside diameter of the tube, m;

P is the design pressure, MPa, determined according to Section 6.2;

[σ] is the allowable stress, MPa, determined according to Section 6.4;

and φw is the strength coefficient; for seamless tubes from which the finned heating surfaces are generally made,

w = 1								(6.4)

6.5.3. The allowable wall thickness [δ] is determined from the design wall thickness with account for the addition term C,

[] = calc + C							(6.5)

The value of C is assumed in accordance with Section 6.5.4.

Table 6.4. Nominal allowable stresses [σ, MPa] for carbon steels with reduced content of P and S.

| T, ºС | Steel grade |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.08 to 0.12% C |  |  |  | 0.15 to 0.16% C |  |  | 0.18 to 0.2% C |  |  |  |
|  | Design service life, h |  |  |  |  |  |  |  |  |  |  |
|  | 104 | 105 | 2105 | 3105 | 104 | 105 | 2105 | 104 | 105 | 2105 | 3105 |
| 20 - 100 | - | 130 | - | - | - | 140 | - | - | 147 | - | - |
| 200 | - | 120 | - | - | - | 130 | - | - | 140 | - | - |
| 250 | - | 108 | - | - | - | 120 | - | - | 132 | - | - |
| 275 | - | 102 | - | - | - | 113 | - | - | 126 | - | - |
| 300 | - | 96 | - | - | - | 106 | - | - | 119 | - | - |
| 320 | - | 92 | - | - | - | 101 | - | - | 114 | - | - |
| 340 | - | 87 | - | - | - | 96 | - | - | 109 | - | - |
| 350 | - | 85 | - | - | - | 93 | - | - | 106 | - | - |
| 360 | - | 82 | - | 82 | - | 90 | - | - | 103 | - | 103 |
| 380 | - | 76 | 76 | 71 | - | 85 | 85 | - | 97 | 97 | 88 |
| 400 | 73 | 73 | 66 | 60 | 80 | 80 | 72 | 92 | 92 | 78 | 71 |
| 410 | 70 | 68 | 61 | 55 | 77 | 72 | 65 | 89 | 86 | 70 | 63 |
| 420 | 68 | 62 | 57 | 50 | 74 | 66 | 58 | 86 | 79 | 63 | 56 |
| 430 | 66 | 57 | 51 | 45 | 71 | 60 | 52 | 83 | 72 | 57 | 50 |
| 440 | 63 | 51 | 45 | 40 | 68 | 53 | 45 | 80 | 66 | 50 | 44 |
| 450 | 61 | 46 | 38 | 35 | 65 | 47 | 38 | 77 | 59 | 46 | 39 |
| 460 | 58 | 40 | 33 | 29 | 62 | 40 | 33 | 74 | 52 | 38 | 34 |
| 470 | 52 | 34 | 28 | 24 | 54 | 34 | 28 | 64 | 46 | 32 | 28 |
| 480 | 45 | 28 | 22 | 18 | 46 | 28 | 22 | 56 | 39 | 27 | 24 |
| 490 | 39 | 24 |  |  | 40 | 24 |  | 49 | 33 |  |  |
| 500 | 33 | 20 |  |  | 34 | 20 |  | 41 | 26 |  |  |
| 510 | 26 |  |  |  |  |  |  | 35 |  |  |  |

Table 6.5. Nominal allowable stresses [σ, MPa] for heat-resistant steels with content of Cr and Mo less than 1%.

| T, ºС | Steel grade |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.12% C |  |  |  | 0.15% C |  |  |  |
|  | Design service life, h |  |  |  |  |  |  |  |
|  | 104 | 105 | 2105 | 3105 | 104 | 105 | 2105 | 3105 |
| from 20 to 100 | - | 147 | - | - | - | 153 | - | - |
| 250 | - | 145 | - | - | - | 152 | - | - |
| 300 | - | 141 | - | - | - | 147 | - | - |
| 350 | - | 137 | - | - | - | 140 | - | - |
| 400 | - | 132 | - | - | - | 133 | - | - |
| 420 | - | 129 | - | - | - | 131 | - | - |
| 440 | - | 126 | - | - | - | 128 | - | - |
| 450 | - | 125 | - | - | - | 127 | - | - |
| 460 | - | 123 | 123 | 123 | - | 125 | 125 | 125 |
| 480 | 120 | 120 | 102 | 90 | 122 | 122 | 113 | 103 |
| 500 | 116 | 95 | 77 | 64 | 119 | 105 | 85 | 76 |
| 510 | 114 | 78 | 60 | 53 | 117 | 85 | 72 | 62 |
| 520 | 107 | 66 | 49 | 43 | 110 | 70 | 58 | 50 |
| 530 | 93 | 54 | 40 | 35 | 97 | 56 | 44 | 39 |
| 540 | 77 | 43 |  |  | 80 | 45 | 35 | 31 |
| 550 | 60 |  |  |  | 62 | 35 | 26 | 23 |
| 560 |  |  |  |  | 52 | 27 |  |  |
| 570 |  |  |  |  | 42 | 21 |  |  |
| 580 |  |  |  |  |  |  |  |  |
| 590 |  |  |  |  |  |  |  |  |
| 600 |  |  |  |  |  |  |  |  |
| 610 |  |  |  |  |  |  |  |  |
| 620 |  |  |  |  |  |  |  |  |

Notes:

1. Underlined values are stresses determined from the yield stress as a function of temperature.

2. The allowable stresses in the columns for service lives of 104, 2105 and 3105 h, marked by the sign “” above the bar, are taken to be equal to the values in the column for a service life of 105 h.

3. The allowable pressures with an overbar correspond to the operation of elements under the conditions of creep and are determined from the limit of the long-term strength for a pertinent service life.

6.5.4. The additive to the design wall thickness C is made up of the manufacturing C1 and operational C2 additives

C=C1+C2	                       			(6.6)

C1 is determined according to Section 6.5.5, and C2 according to Section 6.5.6.

6.5.5. The manufacturing additive C1 consists of additives that make up for a possible decrease in the strength of the detail during its fabrication due to a minus deviation of the wall thickness of the semifinished product C11 and to technological thinnings C12 ,

C1=C11+C12		               		(6.7)

The value of the additive C11 should be determined from the limiting minus deviation of the wall thickness of tubes of the preselected dimension type, established by standards or specifications. If such data are not available, it can be assumed that

C11 = 0.15ˑt						(6.8)

The value of the additive C12 is determined by the technology of manufacturing the detail and assumed according to relevant technical conditions. For seamless steel tubes, it can be assumed that

C12=0					(6.9)

6.5.6. The operational additive consists of additives that make up for a decrease in the tube strength under operational conditions due to corrosion and erosion from the side of the internal medium C21 and from the side of the external medium C22 ,

C2=C21+C22				(6.10)

The value of the additive C21 for tubes made of carbon and low-alloy heat-resistant steels with a design service life of 105 h is determined from Table 6.5 according to the outside diameter of tubes d and the type of the internal medium.

The value of the additive C22 in the general case depends on the temperature of the outside surface of the tube T1, the composition of the external heat-transfer medium (combustion products) and the type of metal (the grade of steel), of which the tube is made. In order to determine the additive C22 , the temperature of the outside surface of the tube t1 should be compared with the allowable temperature [T1], whose values for carbon and low-alloy heat-resistant steels are presented in Table 6.2 with reference to combustion products of the main power-generating fuels.

Table 6.7. Values of the Additive C21.

| Working medium | D 32 mm | 32 mm d 76 mm |
| --- | --- | --- |
| Water, steam-water mixture, dry saturated steam | 0 | 0.5 mm |
| Superheated steam | 0 | 0.3 mm |

The value of the additive C22 for the service life of the heating service equal to 105 h should be assumed minimum, proceeding from the conditions

for T1 T1  - 40ºС	С1+С2  0.5 mm; 			(6.11)

for T1  - 40ºСT1 T1	С1+С2  1.0 mm.			(6.12)

For example, if T1< {[T1] - 40°C}, C11 = 0.3 mm, C12 = 0 and C21 = 0.5 mm, then, C11 + C12 + C21 = 0.8 mm and, for condition (6.11) to be fulfilled, the additive C22 should be taken to be zero (C22 = 0). If at the same values of T1 and [T1] C11 = 0.3 mm, C12 = 0 and C21 = 0, then, C11 + C12 + C21 = 0.3 mm and for condition (6.11) to be fulfilled, it is necessary to assume C22 = 0.2 mm.

The value of the additive C22 for general-purpose tubes made of carbon steel should be at least 0.4 mm, regardless of the surface temperature, steel grade and quality.

For a service life shorter than 105 h, it is admissible to decrease the value of the additive C22  in proportion to the ratio of a given service life to that equal to 105 h.

6.5.7. The value of the allowable wall thickness [δ], obtained in accordance with paras 6.5.2 – 6.5.6, is compared with the preliminarily adopted nominal value of the wall thickness of tubes of the calculated finned heating surface δt . The nominal wall thickness should not be smaller than the allowable value,

t  []						(6.13)

7. EXAMPLES OF CALCULATIONS

7.1. Calculation Assignment

To perform the designing of a Water-to-Air Heat Exchanger (WAHE) for a Turbo-Refrigerating Unit (TRU) with the following characteristics:

| air temperature at the inlet |  | = 95ºС |
| --- | --- | --- |
| air temperature at the outlet |  | = 40ºС |
| air pressure at the inlet |  | Рaire = 0.2 МPа |
| total air pressure loss in WAHE |  | h 0.001 МPа |
| temperature of cooling water at WAHE inlet |  | T = 25ºС |
| air flow rate |  | Gg = 2.7 kg/s |
| water flow rate |  | Gf = 3.0 kg/s |
| water pressure at inlet |  | Рf = 0.5 МPа |
| hydraulic resistance of WAHE water conduit |  | el 0.01 МPа |
| overall dimensions of gas conduit (abc),no larger than |  | 0.6 m 0.5 m 1.0 m |

7.2. Heat Balance

The thermal power of WAHE is determined from the equation

where cp is the specific heat of air at Pg = 0.2 MPa in the temperature range  = 40  95°C.

According to Standards (1999), in the above range

as a result,

kW

From the equation of heat balance

the water enthalpy and temperature at the WAHE outlet are determined as follows. In accordance with Table S.2, on the basis of the inlet pressure P = 0.5 MPa and the inlet temperature T = 25°C, the water enthalpy at the WAHE inlet is assumed

then,

in accordance with Table S.2,

ºC

The average water temperature in WAHE is

ºC

The average air temperature in WAHE is

ºC

The physical properties of water at P= 0.5 MPa and T = 31°C (according to Lokshin et al. (1978)) are as follows:

| - density | f = 1000 kg/m3 |
| --- | --- |
| - specific volume | f = 0.001 m3/kg |
| - kinematic viscosity | f = 0.78310-6 m2/s |
| - thermal conductivity | kf = 0.619 W/mК |
| - Prandtl number | Prf = 5.292 |

The physical properties of air at Pm = 0.2 MPa and  = 67.5°C (according to Standards (1999)) are as follows:

| - density | g = 2.049 kg/m3 |
| --- | --- |
| - specific volume | g = 0.488 m3/kg |
| - kinematic viscosity | g = 0.994510-5 m2/s |
| - specific heat | Cр = 1.010 kJ/kgК |
| - thermal conductivity | kg = 0.0294 W/mК |
| - thermal diffusivity | g = 1.41610-5 m2/s |
| - Prandtl number | Prg = 0.702 |

7.3. Structural Features of WAHE

WAHE is designed as a staggered bundle of tubes with external helical finning. The tubes are joined into coils longitudinal with respect to the air passing, whose bends are located outside the gas conduit (Figure 7.1).

Figure 7.1. Sketch of designed WAHE.

Bimetallic tubes with the following characteristics are selected:

the internal tube:

| - material | carbon steel used in steam generators; |
| --- | --- |
| - inside diameter | din = 0.020 m; |
| - wall thickness | t = 2.510-3 m; |

the external tube with rolled helical finning:

| - material | aluminum; |
| --- | --- |
| - diameter of the finning-carrying tube | din = 0.028 m; |
| - fin height | lr = 0.0135 m; |
| - fin spacing | sr = 0.003 m; |
| - average fin thickness | r = 8 10-4 m; |
| - thermal contact resistanceon steel-aluminum interface | Rcont = 1.8910-4 m2KW. |

7.3.1. Specific geometric characteristics of finned tubes

Specific characteristics of finned tubes in the considered case are determined taking into account that the coil bends will be located outside the gas conduit and, as a consequence,

Atotal = A

The surface area of fins per 1 meter of the tube length (according to Eq. (2.3) is

The surface area of the carrying tube, not occupied by fins, per 1 meter of the length of the finned tube is

The area of the outside surface per 1 meter of the tube length is

The ratio Ar /A is

The ratio At /A is

The total surface area of the finning-carrying tube per 1 meter of the tube length is

The area of the inside surface per 1 m of the tube length is

the ratio A/Ain is

The fin coefficient Ψr  is

7.3.2. Dimensions of gas conduit and spacing characteristics of WAHE.

Taking into account the limitations on overall dimensions of the heat exchanger, we select a maximally dense “equilateral” arrangement of the bundle, with which the longitudinal and the transverse tube spacings are related as

(*)

We also assume dimensions of the gas conduit guided by the specified limitations on size:

- width of gas circuit a = 0.056 m,

- height of gas conduit b = 0.050 m

The transverse tube spacing S1 is chosen with account for the maximum transverse dimension of the finned tube, i.e., the outside diameter of finning

and also for the need for the observance of equality of the number of tubes z1 in all transverse rows of the bundle,

D = 0.055 m;

here, z1 = 9 is the maximum number of finned tubes that fit into the width n = 0.56 m with a sufficient technological clearance.

With allowance for relation (*), the longitudinal tube spacing is

The diagonal tube spacing with an “equivalent” arrangement is equal to the transverse tube spacing,

Thus, we finally assume:

the transverse tube spacing S1 = 0.059 m,

the longitudinal tube spacing S2 = 0.051 m,

and the diagonal tube spacing  = 0.059 m.

The relative spacing characteristics are

;                    ;

;                               .

7.3.3. Free area for passage of air and calculated air velocity.

In accordance with Section 2.4.2, in order to determine the minimum free area for the passage of the external heat transfer medium with a staggered arrangement of tubes, we find the conventional diameter of the finned tube (Eq. 2.22)

and afterwards the bundle diameter (Eq. 2.21)

For φcl ≤ 2, the minimum free area is situated in the plane of transverse spacing and is equal to (Eq. 2.23)

here, the length of tubes within the confines of the gas conduit is taken to be equal to its height

According to Section 7.2, the average specific volume of air at Pg = 0.2 MPa and  = 67.5ºС is

The calculated air velocity is

7.3.4. Free area for passage of water and average water velocity.

In accordance with Section 2.5.2, the free area for the passage of the internal heat-transfer medium is obtained from Eq. (2.48), in which the number of tubes, connected in parallel, ztcp is determined by the number of tubes in the transverse row of the bundle z1 and by the number of the coil starts nx. With a staggered arrangement of tubes,

nx  2;

we assume nx = 2, then,

According to Eq. (2.47), the average water velocity is

7.4. Calculation of Area of Heat-Transfer Surface

7.4.1. In accordance with Section 2.1.1, the area of the heat-transfer surface of WAHE can be found from Eq. (2.1)

for which purpose it is necessary to calculate the overall heat transfer coefficient U and the average temperature difference ΔT.

7.4.2. Overall heat transfer coefficient.

According to Section 2.2.1, the overall heat transfer coefficient should be determined from Eq. (2.6)

In this equation, according to Section 2.6.6, the thermal efficiency ψ (the heat-transfer medium is clean air) is taken to be

= 0.95.

In determining the thermal resistance of the wall of bimetallic tubes, it is possible to disregard the quantities  and  owing to their

smallness and to assume RT ≈ Rcont. According to the data sheet, the thermal contact resistance is Rcont≈ 1.89104. Thus, it can be assumed that

RT= Rcont= 1.8910-4  .

Following Section 7.3.1 of the present calculation, the ratio is

.

7.4.3. Reduced heat transfer coefficient h1rdc .

According to Section 2.3.1, when finned tubes are washed by the flow of a clean heat-transfer medium (air), h1rdc should be determined from Eq. (2.10)

The calculation of h1rdc should be started with determining the convective heat transfer coefficient hc , since E and ψE  are also functions of hc .

a) The convective heat transfer coefficient hc .

In accordance with Section 2.4.4, the shape parameter of the bundle X is determined, which for a staggered arrangement of tubes is (Eq. 2.31)

The exponent n and the factor Cq in Eq. (2.28) are obtained from Eqs. (2.29) and (2.30), respectively,

The number of transverse tube rows in the bundle is taken to be z2 > 10. Then, the factor Cz in Eq. (2.28) is

Cz = 1.0.

Substituting the obtained values of m, Cq and Cz , as well as the physical properties of air from Section 7.2 of the present calculation, into Eq. (2.28) yields the following value of hc :

b) The true efficiency of the fin.

According to Section 2.3.1, the true efficiency of the fin is defined by the product EμrψE.

For determining the first multiplier, i.e., the theoretical efficiency of the fin, the fin parameter  needs to be calculated (Eq. 2.13). For this, in turn, it is necessary to know the thermal conductivity of the fin at its average temperature Tr. Let us evaluate Tr according to Eq. (2.16), assuming with a possible subsequent refinement E ≈ 0,9,

Tr = TЕ = 67.5 67.5  310.9  28ºС;

at Tr = 28°C, the thermal conductivity of aluminum is kr = 225 W/mK. Then,

the conventional fin height  is determined from Eq. (2.14)

The theoretical efficiency of the fin is

evidently, there is no need for further refinement of the value of kr .

The correction factor ψE is determined from Eq. (2.15)

The coefficient μr for fins with an approximately constant thickness is taken to be μr = 1.0 (Figure 2.1).

Substituting the obtained values of hc, E, μrand ψE , as well as the values of Ar/H and At / H from Section 7.3.1 of the present calculation, into Eq. (2.10) gives the reduced heat transfer coefficient

7.4.4. Coefficient of heat transfer from wall to internal medium h2.

According to Section 2.5.2, in order to determine h2 it is necessary to know the Reynolds (Rem) and Prandtl (Prm) numbers. According to Sections 7.2 and 7.3.4, Prf = 5.292, νf = 0.783106 m2/s and uf = 0.53 m/s. Then,

At such Ref and Prf numbers, the heat transfer coefficient h2 should be calculated from Eq. (2.43). For this purpose, the quantities  (Eq. 2.44) and ζ (Eq. 2.45) are determined that enter into expression (2.43)

In order to determine the correction Ctem in Eq. (2.43), the average temperature of the inside surface of the tube Tin is evaluated assuming, with a subsequent refinement, the area of the outside heat transfer surface A = 100 m2 and the heat transfer coefficient

h = 3500 W/m2K). Then, with account for Section 7.3.2 and Eq. (2.50a),

for the considered case where the internal heat-transfer medium is dropping liquid (water) and it is heated (the heat flux is directed from the tube wall to water), the correction Ctem is determined from the equation

the dynamic viscosity of water at Рf = 0.5 MPa and Tf = T = 31°C (according to Lokshin et al. (1978)) is

f = 0.78310-3 Pas;

the dynamic viscosity of water at Рf = 0,5 MPa and Tin = = 40°C [9] is

in = 0.651010-3 Pаs;

in view of this,

Next, the values of the obtained quantities are substituted into Eq. (2.43),

Returning to Section 7.4.2, we determine the heat transfer coefficient

7.4.5. Average temperature difference Δt.

We assume a countercurrent scheme of motion of the heat-exchanging media. According to Section 2.7.2, in this case Δt is calculated from Eq. (2.53),in which

Tl = = 95 –37 = 58.0 ºС;

Tsm = = 40 –25 = 15.0 ºС.

As a result,

7.4.6. Results of thermal calculations

a) Returning to Section 7.4.1, we determine the area of the heat transfer surface of WAHE

b) The value of the correction Ctem in the equation for α2 (Section 7.4.4) is refined as follows:

As seen, Tin ≈ T  and there is no need for refining the value of Ctem: Ctem = 1.021.

c) The total length of finned tubes (with no bends) of WAHE is determined

d) The total number of tubes in WAHE is

e) The number of transverse rows of tubes is

we assume z2 = 18.

f) The depth of the gas conduit is

g) The actual number of tubes in WAHE is

h) The actual length of finned tubes of WAHE is

7.5. Calculation of Aerodynamic Resistance

7.5.1. According to Section 3.1.1, the calculation of the aerodynamic resistance should be started with determining the reduced length of the developed surface  and the equivalent diameter of the most contracted cross section of the bundle deq.

The quantity  is calculated from Eq. (3.9),

The equivalent diameter for staggered bundles of tubes with φcl ≤ 2 is determined from Eq. (3.10),

7.5.2. The resistance coefficient ζ0 is calculated using Eq. (3.2) that is valid in the case of staggered arrangement of tubes in the bundle. We now determine the exponent n (Eq. (3.3)), the factor Cr (Eq. (3.4)) and the factor C (Eqs. (3.13) and (3.15)), entering into Eq. (3.2),

, sincez2 = 18, that isz2 6.

According to Eq. (3.2), the resistance coefficient of the bundle ζ0 is determined

7.5.3. Using Eq. (3.1), the aerodynamic resistance of WAHE is calculated

7.6. Calculation of Hydraulic Resistance of WAHE

7.6.1. Geometric characteristics needed for calculations (Figure 7.1)

Water moves in 18 coils connected in parallel. The calculation is performed for a single coil.

The total length of the coil L0 is composed of the lengths of heated Lh and unheated Lun segments,

In the considered case, the length of the heated part of the coil Lh is made up of the lengths of straight finned segments within the confines of the gas conduit Lc.cr.s, arrangement of the bundle is

then,

The length of the unheated part lun in the considered case is composed of the lengths of the segment of withdrawal from the supply collector lwdr and the segment of feed to the intake collector lfd (Figure 7.1), and the lengths of bends lbnd ,

the number of the coil bends with a staggered arrangement of tubes in the bundle is

the length of a single bend is

the bend radius R in the case of staggered arrangement is equal to the longitudinal tube spacing

;

the lengths of the feed and withdrawal segments are taken to be

;

thus,

In WAHE, the medium is fed and withdrawn through horizontal collectors with the inside diameter dcol = 0.081 m and the wall thickness δcol = 0.004 m. The medium feed to the supply collector and the medium withdrawal from the intake collector are end-type, with a full cross section to one side, i.e. a П-shaped scheme of the medium motion is implemented in WAHE.

Since a monophase medium - water - moves in WAHE, its hydraulic resistance is calculated using equations for monophase media.

7.6.2. Calculation of hydraulic resistance of coil ΔPcoil.

- Coefficient of hydraulic friction resistance ζfr.

According to Section 4.4.2, in order to determine ζfr it is necessary to select a value of the absolute roughness of tubes  from Table 4.1. Since the interior of bimetallic tubes is made of carbon steel (Section 7.3), then,  = 8.0105 m.

The relative roughness of tubes is

;    ;

The boundary of the self-similar region of the resistance law at such relative roughness corresponds to the following boundary value of the Reynolds number:

.

Since the actual value of the Reynolds number,Ref (Section 7.4.4) is smaller than the boundary value

= 13,358 ,

ζfr should be determined from Figure 4.1,

at= 13,358 and -fr = 0.0325.

b) Resistance coefficient of the entrance to the heated tube ζent .

In the considered case, there is an end feed of the medium to the supply collector (Figure 4.3, 2) and therefore, according to Section 4.5.2 and Table 4.2,

0.1 and ent = 0.7.

c) Resistance coefficient of the exit from the heated tube to the intake collector ζex .

According to Section 4.5.3 and Table 4.3,

ex = 1.1.

d) Resistance coefficients of turns (bends) ζbnd .

The resistance coefficient of a bend is determined as a function of the angle of turn in the bend φ and of the relative radius of the bend R/din according to Section 4.5.4, Table 4.4 or Figure 4.4.

In all bends, the flow turns through the same angle φ = 180°,

According to Section 7.6.1,

R = 0.051 m, ;

then, according to Table 4.4,

bnd =0.356.

The total resistance coefficient of the coil bends is

e) The hydraulic resistance of the coil.

Since the water density is practically invariable along the entire length of the coil and its velocities in the characteristic cross sections are equal, the hydraulic resistance of the tube part of WAHE can be determined as follows:

7.6.3. Total pressure loss in supply and intake collectors of WAHE .

In accordance with Section 4.6.4, for determining  it is necessary to know maximum variations in the static pressure in the supply  and intake  collectors, which are calculated according to Section 4.6.3.

The free areas of the collectors are

Maximum velocities of water in the supply and intake collectors are practically identical, since its density in the considered temperature range is constant,

From Table 4.6, the coefficient B is determined that takes account of the pressure loss in the collector:

- for the supply collector (with an end feed with a full cross section), Bsup = 0.8;

- and for the intake collector (with an end withdrawal), Bint = 2.0.

The maximum variation in the static pressure in the supply collector of WAHE is

The maximum variation in the static pressure in the intake collector is

According to Section 4.6.4,  with a П-shaped scheme of the medium motion in the element is determined from Eq. (4.16),

7.6.4. Total hydraulic resistance of WAHE Рel .

According to Section 4.2, the total hydraulic resistance of the tube element is made up of the hydraulic resistance of the tube part of the element (the coil) Рcoil and the total pressure loss in its collectors ,

7.6.5. Conclusions based on calculations

Comparing the calculated results with the calculation assignment, it can be concluded that the WAHE structure, adopted in the first version, does not comply with limitations on its aerodynamic resistance,

H = 1400 Pа  Had = 1000 Pa.

We now perform the calculation for the second version of the WAHE structure, differing from the first by the arrangement of tubes in the bundle. In lieu of the maximally dense “equilateral” arrangement, a staggered arrangement is assumed that corresponds to a maximum value of the coefficient of convective heat transfer from the outside αc at the specified fin coefficient of tubes ψr = 14.6. Using recommendations in Section 2.4.5, the ratio of transverse and lateral tube spacings is determined that complies with this condition,

Leaving the dimensions of the gas conduit unchanged (a = 0.56 m and b = 0.50 m), we determine the absolute values of tube spacings,

;

here, z1 = 6 is the maximum number of finned tubes, fitting into the width a = 0.56 m with the ratio of tube spacings (S1 /S2 ) = 2.08 and a sufficient technological clearance between tubes. In the considered case, the minimum clearance between tubes is determined by the finning diameter D and the diagonal tube spacing S,

D = 0.055 m

The results, calculated for the second WAHE version in Sections 7.3.2 – 7.6.4, as compared with those for the first WAHE version, are presented in Table 7.1.

Table 7.1. Calculation results

| No. | Determined quantity | Sorce | Designation | Calculated results |  | Unit |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Ver. 1 | Ver. 2 |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| Calculation of heat transfer |  |  |  |  |  |  |
|  | Transverse tube spacing | - | S1 | 0.059 | 0.086 | m |
|  | Longitudinal tube spacing | - | S2 | 0.051 | 0.041 | m |
|  | Diagonal tube spacing | - | S2 | 0.059 | 0.059 | m |
|  | Ratio of tube spacings | - | S1/S2 | 1.16 | 2.10 | - |
|  | Number of tubes in transverse row of bundle | - | z1 | 9 | 6 | items |
|  | Conventional diameter of finned tube | (2.22) | dcl | 0.0352 | 0.0352 | m |
|  | Parameter of tube bundle | (2.21) | cl | 1.0 | 2.13 | - |
|  | Flow areafor air | (2.23) (2.24) | F | 0.1216 | 0.1638 | m2 |
|  | Calculated air velocity | (2.20) | ug | 10.84 | 8.04 | m/s |
|  | Number of tubes connected in parallel | (2.49) | ztcp | 18 | 12 | - |
|  | Flow areafor water | (2.48) | F | 5.6610-3 | 3.7810-3 | m2 |
|  | Average water velocity in tubes | (2.47) | uf | 0.53 | 0.79 | m/s |
|  | Thermal efficiency | Section 2.6.6 |  | 0.95 | 0.95 | - |
|  | Thermal contact resistance | - | Rcont | 1.8910-4 | 1.8910-4 |  |
|  | Ratio of outside and inside surface areas of finned tubes | - |  | 20.45 | 20.45 | - |
|  | Shape factor of bundle | (2.31) | Х | -0.926 | 0 | - |
|  | Exponent in Reynolds number | (2.29) | n | 0.715 | 0.773 | - |
|  | Factor in equation for hc | (2.30) | Cq | 0.0725 | 0.0472 | - |
|  | Factor taking account of effect of number of transverse tube rows in bundle on heat transfer | (2.37) | Cz | 1.0 | 1.0 | - |
|  | Convective heat transfer coefficient from outside | (2.28) | hc | 123.1 | 115.8 |  |
|  | Average fin temperature | (2.16) | Tr | 28.0 | 28.0 | ºС |
|  | Thermal conductivity of fin | - | kr | 225 | 225 |  |
|  | Fin parameter | (2.13) |  | 36.98 | 35.87 | 1/m |
|  | Conventional fin height | (2.14) |  | 0.0162 | 0.0162 | m |
|  | Theoretical efficiency of the fin | (2.11) | E | 0.895 | 0.901 | - |
|  | Correction factor to theoretical efficiency of fin E | (2.15) | E | 0.985 | 0.985 | - |
|  | Correction factor to theoretical efficiencyof fin E, taking account of fin widening towards base | Figure 2.1 | r | 1.0 | 1.0 | - |
|  | Reduced heat transfer coefficient | (2.10) | h1rdc | 109.2 | 103.4 |  |
|  | Reynolds number for internal heat-transfer medium | - | Ref | 13538 | 20179 | - |
|  | Parameter in equation for h2 | (2.44) | K | 1.066 | 1.045 | - |
|  | Resistance coefficient in equation for h2 | (2.45) |  | 0.0289 | 0.0261 | - |
|  | Correction for effect of temperature dependenceof physical properties of heat-transfer medium onh2 | (2.50) | Ctem | 1.021 | 1.021 | - |
|  | Heat transfer coefficient to internal medium | (2.43) | h2 | 3120 | 4363 |  |
|  | Heat transfer coefficient | (2.6) | U | 48.51 | 52.12 |  |
|  | Average temperature difference | (2.53) | T | 31.8 | 31.8 | ºС |
|  | Calculated area of heat-transfer surface | (2.1) | A | 97.43 | 90.69 | m2 |
|  | Total number of tubes in WAHE | - | z | 162 | 144 | - |
|  | Number of transverse tube rows | - | z2 | 18 | 24 | - |
|  | Depth of gas conduit | - | c | 0.870 | 0.984 | m |
|  | Actual length of finned tubes of WAHE | - |  | 81 | 72 | m |
|  | Actual area of heat transfer surface | - | Aac | 104.0 | 92.4 | m2 |
| Calculation of aerodynamic resistance |  |  |  |  |  |  |
|  | Reduced length of developed surface | (3.9) |  | 53.95 | 25.28 | - |
|  | Equivalent diameter of most contracted cross section of bundle | (3.10) (3.11) | deq | 0.0048 | 0.0095 | m |
|  | Exponent on Reynolds numberReeq | (3.3) | n | 0.330 | 0.273 | - |
|  | Factor in equation for resistance coefficient | (3.4) | Cr | 9.897 | 6.147 | - |
|  | Correction factor taking into account the small number of rows in bundle | (3.15) | Cz | 1.0 | 1.0 | - |
|  | Resistance coefficient of single tube row | (3.2) | 0 | 0.587 | 0.533 | - |
|  | Aerodynamic resistance of WAHE | (3.1) | H | 1400 | 932 | Pа |
| Calculation of hydraulic resistance |  |  |  |  |  |  |
|  | Length of heated segments of coil | - |  | 4.5 | 6.0 | m |
|  | Number of coil bends | - | nbnd | 8 | 11 | - |
|  | Length of unheated segments of coil | - |  | 1.88 | 2.02 | m |
|  | Total length of coil | - |  | 6.38 | 8.02 | m |
|  | Absolute roughness of tubes | Section 4.4.2 |  | 810-5 | 810-5 | m |
|  | Ratiodin/ | - | din/ | 250 | 250 | - |
|  | Friction resistance coefficient | Figure4.1 | fr | 0.0325 | 0.0310 | - |
|  | Inside diameter of collectors | - | dcol | 0.081 | 0.081 | m |
|  | Ratiodin / dcol | - | din / dcol | 0.247 | 0.247 | - |
|  | Resistance coefficient of entrance to heated tube | Table4.2 | ent | 0.7 | 0.7 | - |
|  | Resistance coefficient of exit from heated tube to intake collector | Tabla4.3 | ex | 1.1 | 1.1 | - |
|  | Bend radius | - | R | 0.051 | 0.041 | m |
|  | RatioR/din | - | R / din | 2.55 | 2.05 | - |
|  | Angle of turn of flow in bend | - |  | 180 | 180 | degree |
|  | Resistance coefficient of bend | Tabla 4.4 | bnd | 0.356 | 0.396 | - |
|  | Total resistance coefficient of coil bends | - |  | 2.848 | 4.356 | - |
|  | Hydraulic resistance of coil | - | Рcoil | 2109 | 5800 | Pа |
|  | Free area of collector | - |  | 5.153 10-3 | 5.153 10-3 | m2 |
|  | Maximum medium velocity in collector | - |  | 0.58 | 0.58 | m/s |
|  | Factor taking into account pressure losses in distributing collector | Table 4.6 | Bsup | 0.8 | 0.8 | - |
|  | Factor taking into account pressure losses in intake collector | Table 4.6 | Bint | 2.0 | 2.0 | - |
|  | Maximum variation in static pressurein distributing collector | (4.15) |  | 135 | 135 | Pа |
|  | Max. variation in static pressurein intake collector | (4.15) |  | 336 | 336 | Pа |
|  | Total pressure loss in distributing and intake collectors of WAHE | (4.16) |  | 134 | 134 | Pа |
|  | Total hydraulic resistance of WAHE | (4.5) | Рel | 2243 | 5934 | Pа |

Comparison of the results, calculated for two WAHE versions, indicates that the selection of the rational ratio of the tube spacings in the heat exchanger made it possible to reduce by 50% the aerodynamic resistance of the heat exchanger, which mainly determines the energy consumption during its operation, and to keep within the limits of the imposed restrictions (ΔH< 0.001 MPa). Furthermore, it provided a 12.5% decrease in the mass of the most expensive part of the heat exchanger, i.e., the bundle of bimetallic finned tubes.

REFERENCES

- Pis’mennyi, E.N., 2011. An Asymptotic Approach to Generalizing the Experimental Data on Convective Heat Transfer of Tube Bundles in Crossflow, International Journal of Heat and Mass Transfer, 54 (19-20), pp. 4235-4246.

- Pis'mennyi, E.N., 1996. The Effectiveness of Disk Finning in Tubular Convective Heat Exchangers under Cross-Flow Conditions, Thermal Engineering, 43 (9), pp. 749-753.

- Thermal Calculation of Steam Generators: Standard Method, (In Russian),1973. Editors: N.V. Kuznetsov, V.V. Mitor, E.I. Dubovskoy and E.S. Karasina, ENERGIA Publishing House, Moscow, Russia, 296 pages.

- Portyanko, A.A., Lokshin, V.A., Fomina, V.A., et al., 1980. Experimental Investigations of Tube Bundles Exposed to a Transverse Flow of Gas with Solid Particles, (in Russian), Thermal Engineering (Теплоэнергетика), No. 6, pp. 14-18.

- Fomina. V.N., Titova. E.Ya., Migay. V.K., Bystrov. P.G.. and Pis’mennyi. E.N., 1991. Generalization of Experimental Data and Developmnet of Recommendations for Calculating Heat Transfer in Staggered Tube Bundles with Helical and Circular Fins Exposed to a Transverse Flow of Gas,.(In Russian), Electric Stations (Электрические станции), No. 6, pp. 48-56.

- Migay, V.K., Bystrov, P.G., Pis’mennyi, E.N., and Zoz, V.N., 1987. Generalization of Experimental Data on Convective Heat Transfer and Aerodynamic Resistance in Tube Bundles with Circular Fins, (In Russian), Transactions of TsKTI (Труды ЦКТИ), Leningrad, Russia, No. 236, pp.34-43.

- Pis’mennyi, E.N., 2003. Calculation of Heat Transfer and Aerodynamics inTube Bundles with Circular Fins, (In Russian), ALTERPRES Publishing House, Kiev, Ukraine, 184 pages.

- Standard Methods of Hydraulic Design for Power Boilers, 1988. Editors: V.A. Lokshin, D.F. Peterson, and A.L. Schwarz, Hemisphere Publishing Corporation, Washington, DC, New York, NY, USA, 345 pages.

- Lokshin, V.A., Chakrygin, M.P., Chebulaev, M.M., et al., 1978. On Calculation of Hydraulic Schemes of Steam Overheaters, (in Russian), Thermal Engineering (Теплоэнергетика), No. 1, pp. 81-83.

- Kirilov., P.L., Yuriev, Yu.S., and Bobkov, V.P., 1990. Thermohydraulic Calculations Handbook (Nuclear Reactors), (In Russian), Editors: P.L. Kirilov, Yu.S. Yur’ev, and V.P. Bobkov, 2nd Edition, Augmented and Revised, ENERGOATOMIZDAT Publishing House, Moscow, Russia, 360 pages.

- Vasserman, A.A., Kazavchinskiy, Ya.Z., and Rabinovich, V.A., 1966. Thermophysical Properties of Air and Its Components, (In Russian), NAUKA Publishing House, Moscow, Russia, 376 pages.

- Standard Mechanical Calculation of Power Steam Generators, Steam and Hot Water Piping, (In Russian), 1999. RD 10-249-98, Moscow, Russia, 228 pages.

- Pysmennyy, Ye., Polupan, G., Carvajal Mariscal I., and Sánchez Silva F., 2007. Handbook for Heat Exchangers and Finned Tube Bundles Calculation, (In Spanish), REVERTÉ Publishing House, Mexico City, Mexico, 197 pages.

APPEDICES

APPENDIX A: UNITS CONVERSION

Primary or Fundamental Dimensions and their Units in SI (International System)

| No. | Dimension | Unit |
| --- | --- | --- |
| 1 | Length | meter (m) |
| 2 | Mass | kilogram (kg) |
| 3 | Time | second (s) |
| 4 | Temperature | kelvin (K) |
| 5 | Electric current | ampere (A) |
| 6 | Amount of light | candela (cd) |
| 7 | Amount of matter | mole (mol) |

Standard Prefixes in SI Units

| Multiple | Prefix |
| --- | --- |
| 1012 | tera (T) |
| 109 | giga (G) |
| 106 | mega (M) |
| 103 | kilo (k) |
| 102 | hector (h) |
| 101 | deka (d) |
| 10-1 | deci (d) |
| 10-2 | centi (c) |
| 10-3 | milli (m) |
| 10-6 | micro (μ) |
| 10-9 | nano (n) |
| 10-12 | pico (p) |

Units Conversion

Area

1 m2 = 10.76391 ft2.

1 ft2 = 0.092903 m2; 1 in2 = 6.4516 cm2 = 645.16 mm2; 1 mil2 = 6.452∙10-4 mm2; 1 circular mm = 0.7853982 mm2; 1 circular (circ.) in = 506.707479 mm2; 1 circ. mil = 5.0671∙10-4 mm2; 1 yd2 = 0.8361 m2; 1 acre = 4840 yd2 = 4046.86 m2; 1 mi2 = 2.59 km2.

Density

1 kg/m3 = 6.24280·10–2 lb/ft3.

1 lb/ft3 = 16.0185 kg/m3; 1 slug/ft3 = 515.38 kg/m3.

Electrical Resistivity Specific

1 ohm·circ. mil/ft = 1.6624261·10–9 ohm·m; 1 ohm·in = 0.0254 ohm·m.

Sometimes instead of “Ohm” used a symbol “Ω”.

Energy, Work and Heat Amount

| Units | J* | erg | kgf∙m | kcal | kW∙h |
| --- | --- | --- | --- | --- | --- |
| 1 J=1 W·s | 1.0 | 107 | 0.101972 | 2.38846·10–4 | 2.7778·10–7 |
| 1 erg | 10–7 | 1.0 | 1.01972·10–8 | 2.38846·10–11 | 2.7778·10–14 |
| 1 kgf∙m | 9.80665 | 9.80665·107 | 1.0 | 2.34228·10–3 | 2.724·10–6 |
| 1 kcal | 4.1868·103 | 4.1868·1010 | 4.26935·102 | 1.0 | 1.163·10–3 |
| 1 kW·h | 3.6·106 | 3.6·1013 | 3.67098·105 | 8.59845·102 | 1.0 |

* Units based on names of scientists (researchers etc.) should be capitalized.

1 horse power per hour (h.p.·h) = 2647.8 kJ; 1 electronvolt (eV) = 1.602·10–19 J; 1 erg = 1 dyne (dyn)·cm = 0.1·10–6 J, 1 liter (L, l or ℓ)·atm = 101.33 J.

1 British thermal unit (B.t.u. or BTU) (thermal) = 1.05435 kJ; 1 B.t.u. = 1.055056 kJ; 1 B.t.u. (mean) = 1.05587 kJ.

1 calorie (cal) (thermal) = 4.184 J; 1 cal = 4.1868 J; 1 cal (at 15C) = 4.1858 kJ; 1 cal (at 20C) = 4.1819 J; 1 cal (mean) = 4.19002 J; 1 Calorie (Cal) (food) = 4.1868 kJ.

1 lbf·ft = 1.355817 J; 1 poundal·(pdl) ft = 0.04214 J; 1 therm = 105506 kJ; 1 pound centigrade unit (pcu) = 1.8 B.t.u. = 1.8978 kJ.

Specific Enthalpy

1 kcal/kg = 1 cal/g = 4.1868 kJ/kg; 1 B.t.u./lb = 2.326 kJ/kg; 1 chu/lb = 4.1868 kJ/kg; 1 ft·lbf/lb = 0.00299 kJ/kg.

Flowrate Volumetric (or Volume Flowrate)

1 gallon (US)/min (gpm) = 0.06309 dm3/s; 1 ft3/min (cfm) = 471.95 dm3/s.

Force

1 N = 105 dyn = 0.101972 kgf; 1 kgf  = 9.80665 N.

1 lbf = 4.448222 N; 1 cental = 100 lbf = 444.822 N; 1 kip = 1000 lbf = 4448.222 N; 1 poundal (pdl) = 1 lbf·ft/s2 = 0.138255 N; 1 grain = 0.6355·10–3 N; 1 stone = 62.2751 N.

1 lbf = 0.01 cental = 0.001 kip = 32.174 pdl = 7000.00 grain = 16 ozf.

Heat Flux

1 W/m2 = 0.8598 kcal/h·m2 = 7.988·10–2 kcal/h·ft2 = 0.31791 B.t.u./h·ft2 = 0.17611 centigrades heat unit (chu) /h·ft2.

1 kcal/h·m2 = 1.163 W/m2; 1 cal/s·cm2 = 41868 W/m2.

1 kcal/h·ft2 = 12.5184 W/m2; 1 B.t.u./h·ft2 = 3.154 W/m2; 1 chu/h·ft2 = 5.6783 W/m2.

Heat Flux Volumetric

1 B.t.u./h·ft3 = 10.35 w/m3.

Heat Transfer Coefficient

1 B.t.u. / h·ft2·F = 5.6782 W/m2·K

Heat Transfer Rate and Power

| Units | W | kcal | kgf∙m/s | h.p. (metric) |
| --- | --- | --- | --- | --- |
| 1 W = 1 J/s | 1.0 | 0.86 | 0.102 | 1.36·10–3 |
| 1 kcal/h | 1.163 | 1.0 | 0.118 | 1.58·10–3 |
| 1 kgf∙m/s | 9.81 | 8.44 | 1.0 | 1.33·10–2 |
| 1 h.p. (metric) | 735.5 | 633 | 75 | 1.0 |

1 W = 107 erg/s; 1 m3·atm/h = 28.146 W; 1 h.p. (el.) = 746 W.

1 horse power (h.p.) (UK) = 745.7 W; 1 B.t.u./h = 0.29307 W; 1 lbf·ft/min = 0.022597 W; 1 lbf·ft/s = 1.35582 W; 1 cheval-vapor = 1 h.p. (metric) = 735.5 W; 1 chu/h = 0.52753 W.

Length

1 m = 3.2808 ft.

1 yard (yd) = 0.9144 m = 3 ft (3'); 1 ft = 12 inch (in) (12").

1 ft = 0.3048 m; 1 in (1") = 25.4 mm; 1 mil = 0.001 in = 0.0254 mm; 1 μm = 10–6 m; 1 mile (mi) = 5280 ft = 1609.344 m; 1 nautical mile (nmi) = 6076.1 ft = 1852 m.

Mass

1 pound (lb) = 16 ounces (oz) = 453.59237 g; 1 oz = 28.3495 g; 1 slug = 32.174 lb = 14.594 kg; 1 short ton (or tonne) (t) (US 2000 lb) = 0.9072 metric ton; 1 long ton (imperial ton, UK 2240 lb) = 1.016 metric ton.

Pressure

| Units | Pa | bar | kgf/cm2 | atm (phys.*) | mm Hg | mm H2O |
| --- | --- | --- | --- | --- | --- | --- |
| 1 Pa=1 N/m2 = | 1 | 10–5 | 1.02·10–5 | 0.987·10–5 | 7.5024·10–3 | 0.10197 |
| 1 bar = | 105 | 1.0 | 1.02 | 0.98692 | 7.5024·102 | 1.02·104 |
| 1 kgf/cm2 = 1 at (tech.*) = | 9.80665·104 | 0.980665 | 1.0 | 0.9678 | 735.56 | 104 |
| 1 atm (phys.) = | 1.01325·105 | 1.01325 | 1.0332 | 1.0 | 760.0 | 1.0332·104 |
| 1 mm Hg = 1 torr = | 133.322 | 1.33·10–3 | 1.36·10–3 | 1.316·10–3 | 1.0 | 13.595 |
| 1 mm H2O = 1 kgf/m2 = | 9.80665 | 9.80665·10–5 | 10–4 | 9.678·10–5 | 7.356·10–2 | 1.0 |

* Phys. – physical and tech. – technical.

1 bar = 106 dyn/cm2 = 14.5038 lbf/in2 (psi) = 2088.543 lbf/ft2 = 29.530 inches of Hg = 401.463 inches of water = 1.4504·10–2 kip/in = 69053.14 poundal/ft2.

1 lbf/in2 (pounds per square inch (psiа)) = 6894.76 Pa; 1 lbf/ft2 = 47.88 Pa; 1 inch of Hg = 3.3864 kPa; 1 inch of water = 249.1 Pa; 1 kip/in = 6894.76 kPa.

Specific Heat

1 B.t.u./lb·Ra = 4186.9 J/kg·K; 1 ft·lbf/slug·Ra = 0.16723 J/kg·K.

Temperature Scales

| Scale | K (T) | C (t) | Ra (T) | F (t) | R (t) |
| --- | --- | --- | --- | --- | --- |
| Kelvin K = | 1.0 | t+273.15 | 5/9T | 5/9t+255.37 | 5/4t+273.15 |
| Celsius С = | Т–273.15 | 1.0t | 5/9t–273.15 | 5/9(t–32) | 1.25t |
| Rankine Ra = | 1.8T | 1.8(t+273.15) | 1.0T | t+459.67 | 1.8(1.25t+273.15) |
| Fahrenheit F = | 1.8T–459.67 | 1.8t+32 | T–459.67 | 1.0t | 2.25t+32 |
| Réaumur R = | 0.8(T–273.15) | 0.8t | 0.8(5/9T–273.15) | (t–32)4/9 | 1.0t |

The Rankine temperature scale (widely used in USA, Canada and other countries) is the absolute scale, 0 Ra = 0 K, at the same time 1 Ra = 1F; sometimes degrees of Rankine have a symbol “R”, i.e., for example: 0 R; the same symbol is related to degrees of Réaumur, however, the sign of degree should be used in this case, i.e., 0R.

The temperature scale of Fahrenheit is the practical scale (also widely used in USA, Canada and other countries), 32F = 0C and 212F = 100С.

The Réaumur temperature scale is the practical scale, 0R = 0C, but 80R = 100С (currently, this scale used rarely).

Temperature Difference

ΔT = 1 K = 1C = (9/5) Ra = (9/5)F.

Degrees of absolute scales are more preferable to be used for the temperature difference.

Thermal Conductivity

1 W/m·K = 1 W/m·C = 0.8598 kcal/h·m·С = 2.3885 cal/s·cm·C = 0.5778 B.t.u./h·ft·F = 0.5778 chu/h·ft·C.

1 kcal/h·m·C = 1.163 W/m·K; 1 cal/s·cm·C = 418.68 W/m·K; 1 B.t.u./h·ft·F = 1 chu/h·ft·C = 1.7307 W/m·K; 1 B.t.u.·in/h·F·ft2 = 0.144 W/m·K.

Viscosity Dynamic

| Units | Pa·s | kg/m·s | kgf·s/m2 | P (poise) |
| --- | --- | --- | --- | --- |
| 1 Pa·s=1 N·s/m2 = | 1.0 | 1.0 | 0.101972 | 10.0 |
| 1 kg/m·s = | 1.0 | 1.0 | 0.101972 | 10.0 |
| 1 kgf·s/m2 = | 9.80665 | 9.80665 | 1.0 | 98.0665 |
| P (poise) = | 0.1 | 0.1 | 0.101972·10–1 | 1.0 |

1 Pa·s = 0.671969 lb/ft·s = 2419.088 lb/ft·h = 2.08855·10–2 lbf·s/ft2.

1 lb/ft·s = 1.4882 Pa·s; 1 lb/ft·h = 0.41338·10–3 Pa·s; 1 lbf·s/ft2 = 1 slug/ft·s = 47.8803 Pa·s.

Viscosity Kinematic

1 m2/s = 1·104 St (stokes) = 10.7639 ft2/s = 38750.0775 ft2/h = 91440.0 liter (L, l or ℓ)/in·h;

1 St = 1·10–4 m2/s.

Volume

1 m3 = 35.3147 ft3; 1 ℓ = 1 dm3 = 0.001 m3.

1 ft3 = 0.028317 m3; 1 in3 = 16.3871 cm3; 1 gallon liquid US = 3.7854 ℓ and 1 gallon UK = 4.54609 ℓ; 1 fluid oz (UK) = 28.413 mℓ; 1 fl oz (US) = 29.574 mℓ; 1 pint (pt) (UK) = 0.5683 dm3.

Notes: at – atmosphere (technical), atm – atmosphere (physical), B.t.u. (Btu or BTU) – British thermal unit; cal – calorie, cc – cubic centimeter, chu – centigrades heat unit, 1 circular mil – area of circle with diameter of 1 mil, dyn – dyne, eV – electronvolt, f – force, fl – fluid, ft – foot or feet, h – hour, Hg – mercury, in – inch, J – joule, h – hour, h.p. (hp) – horse power, ℓ (L or l) – liter (litre), lb (from Latin: libra) – pound or lbm (lbm) – pound of mass, lbf (lbf) – pound of force, m – meter (metre), mi – mile; mil – unit of length equal to one thousands of an inch, min – minute, μm – micrometer; N – newton, nmi – nautical mile, oz – once, P – poise, Pa – pascal, pcu – pound centigrade unit, pdl – poundal, psi – pounds per square inch, psia – psi absolute, psig – psi gauge, s – second, St – stoke, UK – United Kingdom (i.e., British unit), US – United States, yd – yard, W - watt.

Some Physical Constants and Definitions

Normal acceleration due to gravity – gn = 9.80665 m/s2 = 32.174 ft/s2;

Universal gas constant – R = 8.31451 J/mol·K = 8.31447 kPa∙m3/kmol∙K = 0.0831447 bar∙m3/kmol∙K = 82.05 L∙atm/kmol∙K = 1.9858 Btu/lbmol∙Ra = 1545.37 ft∙lbf/lbmol∙Ra = 10.73 psia∙ft3/lbmol∙Ra.

Normal conditions – are physical conditions at a pressure of p = 101325 Pa = 1.01325 bar = 14.696 psi = 760 mm Hg (normal atmosphere) = 29.9213 in Hg = 10.3323 m H2O and a temperature of t = 273.15 K = 0С at which a molar gas volume is Vo = 2.24141·10–2 m3/mol.

APPENDIX B: RECOMMENDED THERMOPHYSICAL PROPERTIES SOFTWARE FOR GASES AND LIQUIDS

Thermophysical properties of air, water and other gases and fluids at different pressures and temperatures can be calculated using the NIST software (2010) (http://www.nist.gov/srd/nist23.cfm).

“Version 9.1 includes 121 pure fluids, 5 pseudo-pure fluids (such as air), and mixtures with up to 20 components (this statement is taken from:http://www.nist.gov/srd/nist23.cfm, the website accessed on July 17, 2015):

- The typical natural gas constituents methane, ethane, propane, butane, isobutane, pentane, isopentane, hexane, isohexane, heptane, octane, nonane, decane, undecane, dodecane, carbon dioxide, carbon monoxide, hydrogen, nitrogen, and water.

- The hydrocarbons acetone, benzene, butene, cis-butene, cyclohexane, cyclopentane, cyclopropane, ethylene, isobutene, isooctane, methylcyclohexane, propylcyclohexane, neopentane, propyne, trans-butene, and toluene.

- The HFCs R23, R32, R41, R125, R134a, R143a, R152a, R161, R227ea, R236ea, R236fa, R245ca, R245fa, R365mfc, R1233zd(E), R1234yf, and R1234ze(E).

- The refrigerant ethers RE143a, RE245cb2, RE245fa2, and RE347mcc (HFE-7000).

- The HCFCs R21, R22, R123, R124, R141b, and R142b.

- The traditional CFCs R11, R12, R13, R113, R114, and R115.

- The fluorocarbons R14, R116, R218, R1216, C4F10, C5F12, and RC318.

- The "natural" refrigerants ammonia, carbon dioxide, propane, isobutane, and propylene.

- The main air constituents nitrogen, oxygen, and argon.

- The noble elements helium, argon, neon, krypton, and xenon.

- The cryogens argon, carbon monoxide, deuterium, krypton, neon, nitrogen trifluoride, nitrogen, fluorine, helium, methane, oxygen, normal hydrogen, parahydrogen, and orthohydrogen.

- Water (as a pure fluid, or mixed with ammonia).

- Miscellaneous substances including carbonyl sulfide, diethyl ether, dimethyl carbonate, dimethyl ether, ethanol, heavy water, hydrogen chloride, hydrogen sulfide, methanol, methyl chloride, nitrous oxide, Novec-649, sulfur hexafluoride, sulfur dioxide, and trifluoroiodomethane.

- The xylenes m-xylene, o-xylene, p-xylene, and ethylbenzene.

- The FAMES (fatty acid methyl esters, i.e., biodiesel constituents) methyl oleate, methyl palmitate, methyl stearate, methyl linoleate, and methyl linolenate.

- The siloxanes octamethylcyclotetrasiloxane, decamethylcyclopentasiloxane, dodecamethylcyclohexasiloxane, decamethyltetrasiloxane, dodecamethylpentasiloxane, tetradecamethylhexasiloxane, octamethyltrisiloxane, and hexamethyldisiloxane.

79 predefined mixtures (such as R407C, R410A, and air); the user may define and store others.”

“The mini-REFPROP program is a sample version of the full REFPROP program (located at www.nist.gov/srd/nist23.cfm) and is meant for use as a teaching tool in the introduction of thermodynamics to students.  It contains a limited number of pure fluids (water, CO2, R134a, nitrogen, methane, propane, hydrogen, and dodecane) and also allows mixture calculations of nitrogen with methane for teaching Vapor-Liquid Equilibrium (VLE).  The program expires Aug. 31, 2016, at which point a new set of install files will be uploaded here.” (this statement is taken from: http://www.boulder.nist.gov/div838/theory/refprop/MINIREF/MINIREF.HTM, the website accessed on July 17, 2015).

APPENDIX C: TABLES OF PROPERTIES OF SUBSTANCES

Table A.1. Thermophysical properties of dry air at 1 atm (101.325 kPa).

| t | ρ | i | s | cv | cp | k | μ | Pr | βth∙103 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| °C | kg/m3 | kJ/kg | kJ/kg∙K | kJ/kg∙K | kJ/kg∙K | W/m∙K | µPa∙s | – | 1/K |
| -70 | 1.741 | 202.87 | 6.474 | 0.7163 | 1.0069 | 0.01848 | 13.55 | 0.738 | 4.963 |
| -60 | 1.659 | 212.93 | 6.523 | 0.7163 | 1.0065 | 0.01930 | 14.10 | 0.736 | 4.726 |
| -50 | 1.584 | 223.00 | 6.569 | 0.7163 | 1.0062 | 0.02011 | 14.65 | 0.733 | 4.510 |
| -40 | 1.516 | 233.06 | 6.613 | 0.7164 | 1.0060 | 0.02090 | 15.19 | 0.731 | 4.313 |
| -30 | 1.453 | 243.12 | 6.655 | 0.7165 | 1.0058 | 0.02169 | 15.72 | 0.729 | 4.133 |
| -20 | 1.395 | 253.17 | 6.696 | 0.7166 | 1.0058 | 0.02247 | 16.24 | 0.727 | 3.968 |
| -10 | 1.342 | 263.23 | 6.735 | 0.7169 | 1.0058 | 0.02324 | 16.75 | 0.725 | 3.815 |
| 0 | 1.293 | 273.29 | 6.772 | 0.7171 | 1.0059 | 0.02400 | 17.26 | 0.723 | 3.674 |
| 10 | 1.247 | 283.35 | 6.808 | 0.7175 | 1.0061 | 0.02475 | 17.76 | 0.722 | 3.543 |
| 20 | 1.204 | 293.41 | 6.843 | 0.7178 | 1.0064 | 0.02549 | 18.25 | 0.721 | 3.421 |
| 30 | 1.164 | 303.48 | 6.877 | 0.7183 | 1.0067 | 0.02622 | 18.73 | 0.719 | 3.307 |
| 40 | 1.127 | 313.55 | 6.910 | 0.7188 | 1.0072 | 0.02695 | 19.21 | 0.718 | 3.201 |
| 50 | 1.092 | 323.62 | 6.941 | 0.7194 | 1.0077 | 0.02766 | 19.68 | 0.717 | 3.101 |
| 60 | 1.059 | 333.70 | 6.972 | 0.7201 | 1.0083 | 0.02837 | 20.15 | 0.716 | 3.007 |
| 70 | 1.028 | 343.79 | 7.002 | 0.7208 | 1.0089 | 0.02907 | 20.60 | 0.715 | 2.919 |
| 80 | 0.999 | 353.88 | 7.031 | 0.7217 | 1.0097 | 0.02977 | 21.06 | 0.714 | 2.836 |
| 90 | 0.972 | 363.98 | 7.059 | 0.7226 | 1.0105 | 0.03046 | 21.51 | 0.714 | 2.758 |
| 100 | 0.946 | 374.09 | 7.087 | 0.7236 | 1.0115 | 0.03114 | 21.95 | 0.713 | 2.683 |
| 120 | 0.897 | 394.34 | 7.140 | 0.7258 | 1.0136 | 0.03249 | 22.82 | 0.712 | 2.546 |
| 140 | 0.854 | 414.64 | 7.190 | 0.7283 | 1.0160 | 0.03249 | 23.67 | 0.711 | 2.546 |
| 160 | 0.815 | 434.99 | 7.238 | 0.7311 | 1.0188 | 0.03511 | 24.50 | 0.711 | 2.310 |
| 180 | 0.779 | 455.39 | 7.284 | 0.7342 | 1.0219 | 0.03639 | 25.31 | 0.711 | 2.208 |
| 200 | 0.746 | 475.86 | 7.328 | 0.7376 | 1.0252 | 0.03765 | 26.11 | 0.711 | 2.115 |
| 250 | 0.674 | 527.35 | 7.432 | 0.7472 | 1.0347 | 0.04072 | 28.04 | 0.713 | 1.912 |
| 300 | 0.615 | 579.35 | 7.527 | 0.7580 | 1.0454 | 0.04369 | 29.89 | 0.715 | 1.745 |
| 400 | 0.524 | 685.04 | 7.697 | 0.7815 | 1.0688 | 0.04938 | 33.38 | 0.722 | 1.486 |
| 500 | 0.456 | 793.12 | 7.846 | 0.8054 | 1.0927 | 0.05479 | 36.63 | 0.731 | 1.293 |
| 600 | 0.404 | 903.54 | 7.980 | 0.8282 | 1.1154 | 0.05999 | 39.71 | 0.738 | 1.145 |
| 700 | 0.363 | 1016.10 | 8.103 | 0.8489 | 1.1361 | 0.06502 | 42.64 | 0.745 | 1.027 |
| 800 | 0.329 | 1130.70 | 8.215 | 0.8674 | 1.1545 | 0.06991 | 45.46 | 0.751 | 0.932 |
| 900 | 0.301 | 1247.00 | 8.318 | 0.8836 | 1.1708 | 0.07468 | 48.17 | 0.755 | 0.852 |
| 1000 | 0.277 | 1364.80 | 8.415 | 0.8978 | 1.1850 | 0.07936 | 50.80 | 0.758 | 0.785 |
| 1100 | 0.257 | 1483.90 | 8.505 | 0.9104 | 1.1975 | 0.08395 | 53.35 | 0.761 | 0.728 |
| 1200 | 0.240 | 1604.20 | 8.589 | 0.9214 | 1.2086 | 0.08848 | 55.85 | 0.763 | 0.679 |
| 1300 | 0.224 | 1725.60 | 8.669 | 0.9312 | 1.2184 | 0.09295 | 58.29 | 0.764 | 0.636 |
| 1400 | 0.211 | 1847.90 | 8.744 | 0.9400 | 1.2271 | 0.09738 | 60.69 | 0.765 | 0.598 |

Table A.2. Thermophysical properties of combustion products at 1 atm (101.325 kPa) ( = 0.13,  = 0.11, and  = 0.76).

| t | ρ | i | cp | k | μ | α·106 | ν·106 | Pr |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C | kg/m3 | kJ/kg | kJ/kg·K | W/m·K | μPa·s | m2/s | m2/s | – |
| 0 | 1.295 | 0 | 1.042 | 0.00228 | 15.8 | 16.9 | 12.2 | 0.722 |
| 100 | 0.950 | 105.5 | 1.068 | 0.00313 | 20.4 | 30.9 | 21.5 | 0.696 |
| 200 | 0.748 | 213.8 | 1.097 | 0.00401 | 24.5 | 48.9 | 32.8 | 0.670 |
| 300 | 0.617 | 324.7 | 1.122 | 0.00484 | 28.2 | 69.9 | 45.7 | 0.654 |
| 400 | 0.525 | 438.4 | 1.151 | 0.00570 | 31.7 | 94.3 | 60.4 | 0.640 |
| 500 | 0.457 | 555.2 | 1.185 | 0.00656 | 34.8 | 121.1 | 76.2 | 0.629 |
| 600 | 0.405 | 675.1 | 1.214 | 0.00742 | 37.9 | 150.9 | 93.6 | 0.620 |
| 700 | 0.368 | 797.8 | 1.239 | 0.00827 | 40.7 | 181.4 | 110.6 | 0.610 |
| 800 | 0.330 | 922.9 | 1.264 | 0.00915 | 43.4 | 219.4 | 131.5 | 0.600 |
| 900 | 0.301 | 1050.6 | 1.290 | 0.01000 | 45.9 | 257.5 | 152.5 | 0.592 |
| 1000 | 0.275 | 1180.4 | 1.306 | 0.01090 | 48.4 | 303.5 | 176.0 | 0.580 |
| 1100 | 0.257 | 1311.9 | 1.323 | 0.01175 | 50.7 | 345.6 | 197.3 | 0.571 |
| 1200 | 0.240 | 1445.0 | 1.340 | 0.01262 | 53.0 | 392.4 | 220.8 | 0.563 |
| 1300 | 0.230 | 1580.0 | 1.360 | 0.01351 | 55.0 | 431.9 | 239.1 | 0.554 |
| 1400 | 0.220 | 1717.0 | 1.380 | 0.01440 | 56.5 | 474.3 | 256.8 | 0.541 |
| 1500 | 0.210 | 1856.5 | 1.410 | 0.01530 | 58.6 | 516.7 | 279.1 | 0.540 |
| 1600 | 0.200 | 1999.0 | 1.440 | 0.01620 | 60.0 | 562.5 | 300.0 | 0.533 |
| 1700 | 0.195 | 2144.0 | 1.460 | 0.01705 | 64.5 | 598.9 | 330.8 | 0.552 |
| 1800 | 0.190 | 2291.0 | 1.480 | 0.01810 | 68.6 | 643.7 | 361.1 | 0.561 |
| 1900 | 0.185 | 2440.0 | 1.500 | 0.01895 | 72.2 | 682.9 | 390.3 | 0.572 |
| 2000 | 0.180 | 2591.0 | 1.520 | 0.01985 | 75.4 | 725.5 | 418.9 | 0.577 |

Table A.3. Thermophysical properties of water (liquid) on saturation line (based on temperature increments).

| t | Ps | ρ | i | cp | k | μ·106 | σ·103 | βth·103 | Pr |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C | MPa | kg/m3 | kJ/kg | J/kg·K | W/m·K | Pa·s | N/m | 1/K | – |
| 5.0 | 0.0009 | 999.9 | 21.0 | 4205.5 | 0.571 | 1518.3 | 74.94 | 0.016 | 11.192 |
| 10.0 | 0.0012 | 999.7 | 42.0 | 4195.5 | 0.580 | 1306.0 | 74.22 | 0.088 | 9.447 |
| 15.0 | 0.0017 | 999.1 | 63.0 | 4188.8 | 0.589 | 1137.6 | 73.49 | 0.151 | 8.086 |
| 20.0 | 0.0023 | 998.2 | 83.9 | 4184.4 | 0.598 | 1001.6 | 72.74 | 0.207 | 7.004 |
| 25.0 | 0.0032 | 997.0 | 104.8 | 4181.6 | 0.607 | 890.1 | 71.97 | 0.257 | 6.130 |
| 30.0 | 0.0042 | 995.6 | 125.7 | 4180.1 | 0.615 | 797.4 | 71.19 | 0.303 | 5.416 |
| 35.0 | 0.0056 | 994.0 | 146.6 | 4179.5 | 0.623 | 719.3 | 70.40 | 0.346 | 4.823 |
| 40.0 | 0.0074 | 992.2 | 167.5 | 4179.6 | 0.631 | 653.0 | 69.60 | 0.385 | 4.328 |
| 45.0 | 0.0096 | 990.2 | 188.4 | 4180.4 | 0.637 | 596.1 | 68.78 | 0.423 | 3.910 |
| 50.0 | 0.0124 | 988.0 | 209.3 | 4181.5 | 0.644 | 546.8 | 67.94 | 0.458 | 3.553 |
| 55.0 | 0.0158 | 985.7 | 230.3 | 4183.1 | 0.649 | 504.0 | 67.10 | 0.491 | 3.247 |
| 60.0 | 0.0199 | 983.2 | 251.2 | 4185.1 | 0.654 | 466.4 | 66.24 | 0.523 | 2.983 |
| 65.0 | 0.0250 | 980.5 | 272.1 | 4187.5 | 0.659 | 433.2 | 65.37 | 0.554 | 2.753 |
| 70.0 | 0.0312 | 977.7 | 293.1 | 4190.2 | 0.663 | 403.9 | 64.48 | 0.584 | 2.552 |
| 75.0 | 0.0386 | 974.8 | 314.0 | 4193.3 | 0.667 | 377.7 | 63.58 | 0.613 | 2.376 |
| 80.0 | 0.0474 | 971.8 | 335.0 | 4196.9 | 0.670 | 354.3 | 62.67 | 0.641 | 2.220 |
| 85.0 | 0.0579 | 968.6 | 356.0 | 4200.8 | 0.673 | 333.3 | 61.75 | 0.669 | 2.081 |
| 90.0 | 0.0702 | 965.3 | 377.0 | 4205.3 | 0.675 | 314.4 | 60.82 | 0.697 | 1.958 |
| 95.0 | 0.0846 | 961.9 | 398.1 | 4210.2 | 0.677 | 297.3 | 59.87 | 0.724 | 1.848 |
| 100.0 | 0.1014 | 958.4 | 419.2 | 4215.7 | 0.679 | 281.7 | 58.91 | 0.751 | 1.749 |
| 105.0 | 0.1209 | 954.7 | 440.3 | 4221.7 | 0.681 | 267.6 | 57.94 | 0.777 | 1.660 |
| 110.0 | 0.1434 | 951.0 | 461.4 | 4228.3 | 0.682 | 254.7 | 56.96 | 0.804 | 1.580 |
| 115.0 | 0.1692 | 947.1 | 482.6 | 4235.6 | 0.683 | 242.9 | 55.97 | 0.831 | 1.507 |
| 120.0 | 0.1987 | 943.1 | 503.8 | 4243.5 | 0.683 | 232.1 | 54.97 | 0.858 | 1.441 |
| 130.0 | 0.2703 | 934.8 | 546.4 | 4261.5 | 0.684 | 212.9 | 52.93 | 0.912 | 1.327 |
| 140.0 | 0.3615 | 926.1 | 589.2 | 4282.6 | 0.683 | 196.5 | 50.86 | 0.968 | 1.232 |
| 150.0 | 0.4762 | 917.0 | 632.2 | 4307.1 | 0.682 | 182.5 | 48.74 | 1.027 | 1.152 |
| 160.0 | 0.6182 | 907.5 | 675.5 | 4335.4 | 0.680 | 170.2 | 46.59 | 1.088 | 1.085 |
| 170.0 | 0.7922 | 897.5 | 719.1 | 4367.8 | 0.677 | 159.6 | 44.41 | 1.153 | 1.029 |
| 180.0 | 1.0028 | 887.0 | 763.1 | 4405.0 | 0.673 | 150.1 | 42.19 | 1.222 | 0.982 |
| 190.0 | 1.2552 | 876.1 | 807.4 | 4447.4 | 0.669 | 141.8 | 39.95 | 1.297 | 0.943 |
| 200.0 | 1.5549 | 864.7 | 852.3 | 4495.8 | 0.663 | 134.3 | 37.68 | 1.379 | 0.910 |
| 210.0 | 1.9077 | 852.7 | 897.6 | 4551.2 | 0.657 | 127.6 | 35.38 | 1.469 | 0.884 |
| 220.0 | 2.3196 | 840.2 | 943.6 | 4614.6 | 0.650 | 121.5 | 33.07 | 1.569 | 0.863 |
| 230.0 | 2.7971 | 827.1 | 990.2 | 4687.6 | 0.641 | 116.0 | 30.74 | 1.682 | 0.848 |
| 240.0 | 3.3469 | 813.4 | 1037.6 | 4771.9 | 0.632 | 110.9 | 28.39 | 1.810 | 0.837 |
| 250.0 | 3.9762 | 798.9 | 1085.8 | 4870.1 | 0.621 | 106.1 | 26.04 | 1.958 | 0.832 |
| 260.0 | 4.6923 | 783.6 | 1135.0 | 4985.6 | 0.609 | 101.7 | 23.69 | 2.130 | 0.832 |
| 270.0 | 5.5030 | 767.5 | 1185.3 | 5123.0 | 0.596 | 97.5 | 21.34 | 2.334 | 0.838 |
| 280.0 | 6.4166 | 750.3 | 1236.9 | 5288.9 | 0.581 | 93.5 | 18.99 | 2.581 | 0.851 |
| 290.0 | 7.4418 | 731.9 | 1290.0 | 5493.1 | 0.565 | 89.7 | 16.66 | 2.886 | 0.872 |
| 300.0 | 8.5879 | 712.1 | 1345.0 | 5750.4 | 0.547 | 85.9 | 14.36 | 3.274 | 0.902 |
| 310.0 | 9.8651 | 690.7 | 1402.2 | 6084.8 | 0.529 | 82.2 | 12.09 | 3.784 | 0.946 |
| 320.0 | 11.2840 | 667.1 | 1462.2 | 6537.3 | 0.509 | 78.4 | 9.86 | 4.486 | 1.007 |
| 330.0 | 12.8580 | 640.8 | 1525.9 | 7186.3 | 0.489 | 74.5 | 7.70 | 5.513 | 1.095 |
| 340.0 | 14.6010 | 610.7 | 1594.5 | 8208.0 | 0.469 | 70.4 | 5.63 | 7.175 | 1.234 |
| 350.0 | 16.5290 | 574.7 | 1670.9 | 10116.0 | 0.447 | 65.9 | 3.67 | 10.393 | 1.490 |
| 360.0 | 18.6660 | 527.6 | 1761.7 | 15004.0 | 0.426 | 60.3 | 1.88 | 19.121 | 2.126 |
| 370.0 | 21.0440 | 451.4 | 1890.7 | 45155.0 | 0.425 | 52.1 | 0.39 | 76.384 | 5.532 |

Table A.4. Thermophysical properties of water (vapor) on saturation line (based on temperature increaments).

| t | Ps | ρv | iv | ifg | cpv | kv·102 | μv·106 | βth·103 | Prv |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C | MPa | kg/m3 | kJ/kg | kJ/kg | J/kg·K | W/m·K | Pa·s | 1/K | – |
| 5.0 | 0.0009 | 0.007 | 2510.1 | 2489.0 | 1889.4 | 1.734 | 9.336 | 3.619 | 1.017 |
| 10.0 | 0.0012 | 0.009 | 2519.2 | 2477.2 | 1894.7 | 1.762 | 9.461 | 3.559 | 1.017 |
| 15.0 | 0.0017 | 0.013 | 2528.3 | 2465.4 | 1900.2 | 1.792 | 9.592 | 3.502 | 1.017 |
| 20.0 | 0.0023 | 0.017 | 2537.4 | 2453.5 | 1905.9 | 1.823 | 9.727 | 3.447 | 1.017 |
| 25.0 | 0.0032 | 0.023 | 2546.5 | 2441.7 | 1911.8 | 1.855 | 9.867 | 3.395 | 1.017 |
| 30.0 | 0.0042 | 0.030 | 2555.5 | 2429.8 | 1918.0 | 1.889 | 10.010 | 3.345 | 1.017 |
| 35.0 | 0.0056 | 0.040 | 2564.5 | 2417.9 | 1924.5 | 1.924 | 10.157 | 3.298 | 1.016 |
| 40.0 | 0.0074 | 0.051 | 2573.5 | 2406.0 | 1931.4 | 1.960 | 10.308 | 3.253 | 1.016 |
| 45.0 | 0.0096 | 0.066 | 2582.4 | 2394.0 | 1938.8 | 1.998 | 10.461 | 3.210 | 1.015 |
| 50.0 | 0.0124 | 0.083 | 2591.3 | 2381.9 | 1946.8 | 2.037 | 10.616 | 3.170 | 1.015 |
| 55.0 | 0.0158 | 0.105 | 2600.1 | 2369.8 | 1955.4 | 2.077 | 10.774 | 3.132 | 1.014 |
| 60.0 | 0.0199 | 0.130 | 2608.8 | 2357.7 | 1964.8 | 2.119 | 10.935 | 3.096 | 1.014 |
| 65.0 | 0.0250 | 0.161 | 2617.5 | 2345.4 | 1975.0 | 2.162 | 11.097 | 3.063 | 1.014 |
| 70.0 | 0.0312 | 0.198 | 2626.1 | 2333.0 | 1986.2 | 2.207 | 11.260 | 3.033 | 1.013 |
| 75.0 | 0.0386 | 0.242 | 2634.6 | 2320.6 | 1998.5 | 2.253 | 11.426 | 3.004 | 1.013 |
| 80.0 | 0.0474 | 0.294 | 2643.0 | 2308.0 | 2012.0 | 2.301 | 11.592 | 2.979 | 1.014 |
| 85.0 | 0.0579 | 0.354 | 2651.3 | 2295.3 | 2026.7 | 2.351 | 11.760 | 2.956 | 1.014 |
| 90.0 | 0.0702 | 0.424 | 2659.5 | 2282.5 | 2042.9 | 2.402 | 11.929 | 2.935 | 1.015 |
| 95.0 | 0.0846 | 0.505 | 2667.6 | 2269.5 | 2060.7 | 2.455 | 12.099 | 2.917 | 1.016 |
| 100.0 | 0.1014 | 0.598 | 2675.6 | 2256.4 | 2080.0 | 2.510 | 12.269 | 2.902 | 1.017 |
| 105.0 | 0.1209 | 0.705 | 2683.4 | 2243.1 | 2101.2 | 2.566 | 12.440 | 2.890 | 1.019 |
| 110.0 | 0.1434 | 0.827 | 2691.1 | 2229.6 | 2124.4 | 2.625 | 12.612 | 2.881 | 1.021 |
| 115.0 | 0.1692 | 0.965 | 2698.6 | 2216.0 | 2149.6 | 2.685 | 12.784 | 2.875 | 1.024 |
| 120.0 | 0.1987 | 1.122 | 2705.9 | 2202.1 | 2177.0 | 2.747 | 12.956 | 2.872 | 1.027 |
| 130.0 | 0.2703 | 1.497 | 2720.1 | 2173.7 | 2238.9 | 2.877 | 13.301 | 2.876 | 1.035 |
| 140.0 | 0.3615 | 1.967 | 2733.4 | 2144.3 | 2310.9 | 3.014 | 13.647 | 2.894 | 1.046 |
| 150.0 | 0.4762 | 2.548 | 2745.9 | 2113.7 | 2393.9 | 3.160 | 13.992 | 2.926 | 1.060 |
| 160.0 | 0.6182 | 3.260 | 2757.4 | 2082.0 | 2488.3 | 3.313 | 14.337 | 2.973 | 1.077 |
| 170.0 | 0.7922 | 4.122 | 2767.9 | 2048.8 | 2594.4 | 3.475 | 14.681 | 3.036 | 1.096 |
| 180.0 | 1.0028 | 5.159 | 2777.2 | 2014.2 | 2712.9 | 3.645 | 15.025 | 3.116 | 1.118 |
| 190.0 | 1.2552 | 6.395 | 2785.3 | 1977.9 | 2844.3 | 3.824 | 15.370 | 3.215 | 1.143 |
| 200.0 | 1.5549 | 7.861 | 2792.0 | 1939.7 | 2989.5 | 4.011 | 15.715 | 3.334 | 1.171 |
| 210.0 | 1.9077 | 9.589 | 2797.3 | 1899.6 | 3150.3 | 4.209 | 16.061 | 3.476 | 1.202 |
| 220.0 | 2.3196 | 11.615 | 2800.9 | 1857.4 | 3328.9 | 4.417 | 16.411 | 3.645 | 1.237 |
| 230.0 | 2.7971 | 13.985 | 2802.9 | 1812.7 | 3528.5 | 4.638 | 16.765 | 3.845 | 1.276 |
| 240.0 | 3.3469 | 16.749 | 2803.0 | 1765.4 | 3753.7 | 4.873 | 17.125 | 4.084 | 1.319 |
| 250.0 | 3.9762 | 19.967 | 2800.9 | 1715.2 | 4010.5 | 5.126 | 17.495 | 4.370 | 1.369 |
| 260.0 | 4.6923 | 23.712 | 2796.6 | 1661.6 | 4307.5 | 5.403 | 17.877 | 4.715 | 1.425 |
| 270.0 | 5.5030 | 28.073 | 2789.7 | 1604.4 | 4656.3 | 5.711 | 18.277 | 5.136 | 1.490 |
| 280.0 | 6.4166 | 33.165 | 2779.9 | 1543.0 | 5073.1 | 6.061 | 18.700 | 5.658 | 1.565 |
| 290.0 | 7.4418 | 39.132 | 2766.7 | 1476.7 | 5582.1 | 6.471 | 19.154 | 6.316 | 1.652 |
| 300.0 | 8.5879 | 46.168 | 2749.6 | 1404.6 | 6219.7 | 6.965 | 19.651 | 7.166 | 1.755 |
| 310.0 | 9.8651 | 54.541 | 2727.9 | 1325.7 | 7044.9 | 7.584 | 20.207 | 8.299 | 1.877 |
| 320.0 | 11.2840 | 64.638 | 2700.6 | 1238.4 | 8158.9 | 8.391 | 20.846 | 9.871 | 2.027 |
| 330.0 | 12.8580 | 77.050 | 2666.0 | 1140.2 | 9752.6 | 9.494 | 21.606 | 12.181 | 2.219 |
| 340.0 | 14.6010 | 92.759 | 2621.8 | 1027.3 | 12236.0 | 11.091 | 22.554 | 15.877 | 2.488 |
| 350.0 | 16.5290 | 113.610 | 2563.6 | 892.8 | 16692.0 | 13.595 | 23.820 | 22.688 | 2.925 |
| 360.0 | 18.6660 | 143.900 | 2481.5 | 719.8 | 27356.0 | 18.151 | 25.724 | 39.436 | 3.877 |
| 370.0 | 21.0440 | 201.840 | 2334.5 | 443.8 | 96598.0 | 32.384 | 29.678 | 151.640 | 8.853 |

Table A5. Specific volumes, specific enthalpies and latent heat of vaporization of water (liquid and vapor) on saturation line (based on pressure increments).

| р MPa | ts °С | v m3/kg | vv m3/kg | i kJ/kg | iv kJ/kg | ifg kJ/kg |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0.001 | 7.0 | 0.0010001 | 129.2080 | 29.33 | 2513.8 | 2484.5 |  |
| 0.002 | 17.5 | 0.0010012 | 67.006000 | 73.45 | 2533.2 | 2459.8 |  |
| 0.003 | 24.1 | 0.0010027 | 45.668000 | 101.00 | 2545.2 | 2444.2 |  |
| 0.004 | 29.0 | 0.0010040 | 34.803000 | 121.41 | 2554.1 | 2432.7 |  |
| 0.005 | 32.9 | 0.0010052 | 28.196000 | 137.77 | 2561.2 | 2423.4 |  |
| 0.006 | 36.2 | 0.0010064 | 23.742000 | 151.50 | 2567.1 | 2415.6 |  |
| 0.007 | 39.0 | 0.0010074 | 20.532000 | 163.38 | 2572.2 | 2408.8 |  |
| 0.008 | 41.5 | 0.0010089 | 18.106000 | 173.87 | 2576.7 | 2402.8 |  |
| 0.009 | 43.8 | 0.0010094 | 16.206000 | 183.28 | 2580.8 | 2397.5 |  |
| 0.010 | 45.8 | 0.0010102 | 14.676000 | 191.84 | 2584.4 | 2392.6 |  |
| 0.012 | 49.5 | 0.0010119 | 12.364000 | 206.94 | 2590.9 | 2384.0 |  |
| 0.014 | 52.6 | 0.0010133 | 10.696000 | 220.03 | 2596.4 | 2376.4 |  |
| 0.016 | 55.3 | 0.0010147 | 9.434800 | 231.60 | 2601.3 | 2369.7 |  |
| 0.018 | 57.8 | 0.0010160 | 8.447000 | 242.00 | 2605.7 | 2363.7 |  |
| 0.020 | 60.1 | 0.0010172 | 7.651500 | 251.46 | 2609.6 | 2358.1 |  |
| 0.022 | 62.2 | 0.0010183 | 6.996700 | 260.14 | 2613.2 | 2353.1 |  |
| 0.024 | 64.1 | 0.0010194 | 6.448300 | 268.18 | 2616.6 | 2348.4 |  |
| 0.026 | 65.9 | 0.0010204 | 5.981900 | 275.68 | 2619.7 | 2344.0 |  |
| 0.028 | 67.6 | 0.0010214 | 5.580400 | 282.70 | 2622.6 | 2339.9 |  |
| 0.030 | 69.1 | 0.0010223 | 5.230800 | 289.31 | 2625.3 | 2336.0 |  |
| 0.040 | 75.9 | 0.0010265 | 3.994900 | 317.65 | 2636.8 | 2319.2 |  |
| 0.050 | 81.3 | 0.0010301 | 3.241500 | 340.57 | 2646.0 | 2305.4 |  |
| 0.060 | 86.0 | 0.0010333 | 2.732900 | 359.93 | 2653.6 | 2293.7 |  |
| 0.070 | 90.0 | 0.0010361 | 2.365800 | 376.77 | 2660.2 | 2283.4 |  |
| 0.080 | 93.5 | 0.0010387 | 2.087900 | 391.72 | 2666.0 | 2274.3 |  |
| 0.090 | 96.7 | 0.0010412 | 1.870100 | 405.21 | 2671.1 | 2265.9 |  |
| 0.100 | 99.6 | 0.0010434 | 1.694600 | 417.51 | 2675.7 | 2258.2 |  |
| 0.150 | 111.40 | 0.0010530 | 1.159700 | 467.13 | 2693.9 | 2226.8 |  |
| 0.200 | 120.2 | 0.0010608 | 0.885920 | 504.70 | 2706.9 | 2202.2 |  |
| 0.250 | 127.4 | 0.0010675 | 0.718810 | 535.40 | 2717.2 | 2181.8 |  |
| 0.300 | 133.5 | 0.0010735 | 0.605860 | 561.40 | 2725.5 | 2164.1 |  |
| 0.350 | 138.9 | 0.0010789 | 0.524250 | 584.30 | 2732.5 | 2148.2 |  |
| 0.400 | 143.6 | 0.0010839 | 0.462420 | 604.70 | 2738.5 | 2133.8 |  |
| 0.450 | 147.9 | 0.0010885 | 0.413920 | 623.20 | 2743.8 | 2120.6 |  |
| 0.500 | 151.9 | 0.0010928 | 0.374810 | 640.10 | 2748.5 | 2108.4 |  |
| 0.600 | 158.8 | 0.0011009 | 0.315560 | 670.40 | 2756.4 | 2086.0 |  |
| 0.700 | 1645.0 | 0.0011082 | 0.272740 | 697.10 | 2762.9 | 2065.8 |  |
| 0.800 | 170.4 | 0.0011150 | 0.240300 | 720.90 | 2768.4 | 2047.5 |  |
| 0.900 | 175.43 | 0.0011213 | 0.214840 | 742.60 | 2773.0 | 2030.4 |  |
| 1.000 | 179.9 | 0.0011274 | 0.194300 | 762.60 | 2777.0 | 2014.4 |  |
| 1.100 | 184.1 | 0.0011331 | 0.177390 | 781.10 | 2780.4 | 1999.3 |  |
| 1.200 | 188.0 | 0.0011386 | 0.163200 | 798.40 | 2783.4 | 1985.0 |  |
| 1.300 | 191.6 | 0.0011438 | 0.151120 | 814.70 | 2786.0 | 1971.3 |  |
| 1.400 | 195.0 | 0.0011489 | 0.140720 | 830.10 | 2788.4 | 1958.3 |  |
| 1.500 | 198.3 | 0.0011538 | 0.131650 | 844.70 | 2790.4 | 1945.7 |  |
| 1.600 | 201.3 | 0.0011586 | 0.123680 | 858.60 | 2792.2 | 1933.6 |  |
| 1.700 | 204.3 | 0.0011633 | 0.116610 | 871.80 | 2793.8 | 1922.0 |  |
| 1.800 | 207.1 | 0.0011678 | 0.110310 | 884.60 | 2795.1 | 1910.5 |  |
| 1.900 | 209.8 | 0.0011722 | 0.104640 | 896.80 | 2796.4 | 1899.6 |  |
| 2.000 | 212.8 | 0.0011766 | 0.099530 | 908.60 | 2797.4 | 1888.8 |  |
| 2.100 | 214.8 | 0.0011808 | 0.094880 | 919.90 | 2798.3 | 1878.4 |  |
| 2.200 | 217.2 | 0.0011850 | 0.090640 | 930.90 | 2799.1 | 1868.2 |  |
| 2.300 | 219.5 | 0.0011891 | 0.086760 | 941.60 | 2799.8 | 1858.2 |  |
| 2.400 | 221.7 | 0.0011932 | 0.083190 | 951.90 | 2800.4 | 1848.5 |  |
| 2.500 | 223.9 | 0.0011972 | 0.079900 | 962.00 | 2800.8 | 1838.8 |  |
| 2.600 | 226.0 | 0.0012011 | 0.076850 | 971.70 | 2801.2 | 1829.5 |  |
| 2.700 | 228.1 | 0.0012050 | 0.074020 | 981.20 | 2801.5 | 1820.3 |  |
| 2.800 | 230.0 | 0.0012088 | 0.071380 | 990.50 | 2801.7 | 1811.2 |  |
| 2.900 | 232.0 | 0.0012126 | 0.068920 | 999.50 | 2801.8 | 1802.3 |  |
| 3.000 | 233.9 | 0.0012163 | 0.066620 | 1008.40 | 2801.9 | 1793.5 |  |
| 3.100 | 235.7 | 0.0012200 | 0.064460 | 1017.00 | 2801.9 | 1784.9 |  |
| 3.200 | 237.4 | 0.0012237 | 0.062430 | 1025.50 | 2801.8 | 1776.3 |  |
| 3.300 | 239.2 | 0.0012273 | 0.060520 | 1033.70 | 2801.7 | 1768.0 |  |
| 3.400 | 240.9 | 0.0012310 | 0.058720 | 1041.80 | 2801.5 | 1759.7 |  |
| 3.500 | 242.5 | 0.0012345 | 0.057020 | 1049.80 | 2801.3 | 1751.5 |  |
| 3.600 | 244.2 | 0.0012381 | 0.055400 | 1057.60 | 2801.0 | 1743.4 |  |
| 3.700 | 245.8 | 0.0012416 | 0.053880 | 1065.30 | 2800.7 | 1735.4 |  |
| 3.800 | 247.3 | 0.0012451 | 0.052430 | 1072.80 | 2800.3 | 1727.5 |  |
| 3.900 | 248.8 | 0.0012486 | 0.051050 | 1080.20 | 2799.9 | 1719.7 |  |
| 4.000 | 250.3 | 0.0012521 | 0.049740 | 1087.50 | 2799.4 | 1711.9 |  |
| 4.100 | 251.8 | 0.0012555 | 0.048490 | 1094.60 | 2798.9 | 1704.3 |  |
| 4.200 | 253.2 | 0.0012589 | 0.047290 | 1101.70 | 2798.4 | 1696.7 |  |
| 4.300 | 254.7 | 0.0012623 | 0.046150 | 1108.60 | 2797.8 | 1689.2 |  |
| 4.400 | 256.1 | 0.0012657 | 0.045060 | 1115.50 | 2797.2 | 1681.7 |  |
| 4.500 | 257.4 | 0.0012691 | 0.044020 | 1122.20 | 2796.5 | 1674.3 |  |
| 4.600 | 258.8 | 0.0012725 | 0.043020 | 1128.90 | 2795.9 | 1667.0 |  |
| 4.700 | 260.1 | 0.0012758 | 0.042060 | 1135.40 | 2795.2 | 1659.8 |  |
| 4.800 | 261.4 | 0.0012792 | 0.041140 | 1141.90 | 2794.4 | 1652.5 |  |
| 4.900 | 262.7 | 0.0012825 | 0.040260 | 1148.30 | 2793.6 | 1645.3 |  |
| 5.000 | 263.9 | 0.0012858 | 0.039410 | 1154.60 | 2792.8 | 1638.2 |  |
| 5.200 | 266.4 | 0.0012925 | 0.037800 | 1167.00 | 2791.1 | 1624.1 |  |
| 5.400 | 268.8 | 0.0012990 | 0.036310 | 1179.10 | 2789.3 | 1610.2 |  |
| 5.600 | 271.1 | 0.0013056 | 0.034920 | 1191.00 | 2787.4 | 1596.4 |  |
| 5.800 | 273.4 | 0.0013122 | 0.033630 | 1202.60 | 2785.4 | 1582.8 |  |
| 6.000 | 275.6 | 0.0013187 | 0.032410 | 1213.90 | 2783.3 | 1569.4 |  |
| 6.200 | 277.7 | 0.0013252 | 0.031270 | 1225.10 | 2781.1 | 1556.0 |  |
| 6.400 | 279.8 | 0.0013318 | 0.030200 | 1236.00 | 2778.8 | 1542.8 |  |
| 6.600 | 281.9 | 0.0013383 | 0.029200 | 1246.80 | 2776.4 | 1529.6 |  |
| 6.800 | 283.9 | 0.0013448 | 0.028240 | 1257.30 | 2773.9 | 1516.6 |  |
| 7.000 | 285.8 | 0.0013514 | 0.027340 | 1267.70 | 2771.4 | 1503.7 |  |
| 7.200 | 287.7 | 0.0013579 | 0.026490 | 1278.00 | 2768.7 | 1490.7 |  |
| 7.400 | 289.6 | 0.0013645 | 0.025680 | 1288.00 | 2766.1 | 1478.1 |  |
| 7.600 | 291.4 | 0.0013711 | 0.024920 | 1298.00 | 2763.3 | 1465.3 |  |
| 7.800 | 293.2 | 0.0013777 | 0.024190 | 1307.80 | 2760.4 | 1452.6 |  |
| 8.000 | 295.0 | 0.0013843 | 0.023490 | 1317.50 | 2757.5 | 1440.0 |  |
| 8.200 | 296.7 | 0.0013909 | 0.022830 | 1327.00 | 2754.5 | 1427.5 |  |
| 8.400 | 298.4 | 0.0013976 | 0.022200 | 1336.50 | 2751.4 | 1414.9 |  |
| 8.600 | 300.1 | 0.0014043 | 0.021590 | 1345.80 | 2748.3 | 1402.5 |  |
| 8.800 | 301.7 | 0.0014111 | 0.021010 | 1355.10 | 2745.1 | 1390.0 |  |
| 9.000 | 303.3 | 0.0014179 | 0.020460 | 1364.20 | 2741.8 | 1377.6 |  |
| 9.200 | 305.0 | 0.0014247 | 0.019930 | 1373.20 | 2738.5 | 1365.3 |  |
| 9.400 | 306.5 | 0.0014316 | 0.019420 | 1382.20 | 2735.1 | 1352.9 |  |
| 9.600 | 308.0 | 0.0014385 | 0.018930 | 1391.10 | 2731.6 | 1340.5 |  |
| 9.800 | 309.5 | 0.0014455 | 0.018450 | 1399.90 | 2728.0 | 1328.1 |  |
| 10.000 | 311.0 | 0.0014526 | 0.018000 | 1406.60 | 2724.4 | 1315.8 |  |
| 10.200 | 312.4 | 0.0014597 | 0.017560 | 1417.30 | 2720.8 | 1303.5 |  |
| 10.400 | 313.9 | 0.0014668 | 0.017140 | 1425.80 | 2717.1 | 1291.3 |  |
| 10.600 | 315.3 | 0.0014740 | 0.016740 | 1434.40 | 2713.2 | 1278.8 |  |
| 10.800 | 316.7 | 0.0014813 | 0.016350 | 1442.80 | 2709.4 | 1266.6 |  |
| 11.000 | 318.0 | 0.0014887 | 0.015970 | 1451.20 | 2705.4 | 1254.2 |  |
| 11.200 | 319.4 | 0.0014961 | 0.015600 | 1459.60 | 2701.5 | 1241.9 |  |
| 11.400 | 320.7 | 0.0015036 | 0.015250 | 1467.90 | 2697.3 | 1229.4 |  |
| 11.600 | 322.1 | 0.0015112 | 0.014900 | 1476.20 | 2693.2 | 1217.0 |  |
| 11.800 | 323.4 | 0.0015189 | 0.014570 | 1484.40 | 2689.0 | 1204.6 |  |
| 12.000 | 324.6 | 0.0015267 | 0.014250 | 1492.60 | 2684.8 | 1192.2 |  |
| 12.200 | 325.9 | 0.0015345 | 0.013940 | 1500.70 | 2680.4 | 1179.7 |  |
| 12.400 | 327.2 | 0.0015425 | 0.013630 | 1508.80 | 2676.0 | 1167.2 |  |
| 12.600 | 328.4 | 0.0015506 | 0.013340 | 1516.90 | 2671.6 | 1154.7 |  |
| 12.800 | 329.6 | 0.0015588 | 0.013050 | 1524.90 | 2667.0 | 1142.1 |  |
| 13.000 | 330.8 | 0.0015670 | 0.012770 | 1533.00 | 2662.4 | 1129.4 |  |
| 13.200 | 332.0 | 0.0015755 | 0.012500 | 1541.00 | 2657.7 | 1116.7 |  |
| 13.400 | 333.2 | 0.0015840 | 0.012240 | 1548.90 | 2653.0 | 1104.1 |  |
| 13.600 | 334.3 | 0.0015927 | 0.011990 | 1556.90 | 2648.2 | 1091.3 |  |
| 13.800 | 335.5 | 0.0016015 | 0.011740 | 1564.80 | 2643.3 | 1078.5 |  |
| 14.000 | 336.6 | 0.0016104 | 0.011490 | 1572.80 | 2638.3 | 1065.5 |  |
| 14.200 | 337.8 | 0.0016195 | 0.011260 | 1580.70 | 2633.2 | 1052.5 |  |
| 14.400 | 338.9 | 0.0016288 | 0.011020 | 1588.60 | 2628.1 | 1039.5 |  |
| 14.600 | 340.0 | 0.0016382 | 0.010800 | 1596.50 | 2622.9 | 1026.4 |  |
| 14.800 | 341.0 | 0.0016483 | 0.010570 | 1604.30 | 2617.1 | 1012.8 |  |
| 15.000 | 342.1 | 0.0016580 | 0.010350 | 1612.20 | 2611.6 | 999.4 |  |
| 15.200 | 343.2 | 0.0016680 | 0.010140 | 1620.00 | 2606.1 | 986.1 |  |
| 15.400 | 344.2 | 0.0016782 | 0.009930 | 1627.90 | 2600.4 | 972.5 |  |
| 15.600 | 345.3 | 0.0016886 | 0.009726 | 1635.70 | 2594.6 | 958.9 |  |
| 15.800 | 346.3 | 0.0016992 | 0.009526 | 1643.60 | 2588.7 | 945.1 |  |
| 16.000 | 347.3 | 0.0017101 | 0.009330 | 1651.50 | 2582.7 | 931.2 |  |
| 16.200 | 348.3 | 0.0017212 | 0.009138 | 1659.40 | 2576.6 | 917.2 |  |
| 16.400 | 349.3 | 0.0017327 | 0.008949 | 1667.40 | 2570.4 | 903.0 |  |
| 16.600 | 350.3 | 0.0017444 | 0.008763 | 1675.40 | 2564.0 | 888.6 |  |
| 16.800 | 351.3 | 0.0017565 | 0.008581 | 1683.50 | 2557.5 | 874.0 |  |
| 17.000 | 352.3 | 0.0017690 | 0.008401 | 1691.60 | 2550.8 | 859.2 |  |
| 17.200 | 353.2 | 0.0017818 | 0.008223 | 1699.80 | 2544.0 | 844.2 |  |
| 17.400 | 354.2 | 0.0017951 | 0.006048 | 1708.10 | 2536.9 | 828.8 |  |
| 17.600 | 355.1 | 0.0018069 | 0.007875 | 1716.40 | 2529.7 | 813.3 |  |
| 17.800 | 356.0 | 0.0018231 | 0.007704 | 1724.90 | 2522.2 | 797.3 |  |
| 18.000 | 357.0 | 0.0018380 | 0.007534 | 1733.40 | 2514.4 | 781.0 |  |
| 18.200 | 357.9 | 0.0018534 | 0.007366 | 1742.10 | 2506.3 | 764.2 |  |
| 18.400 | 358.8 | 0.0018696 | 0.007198 | 1750.80 | 2497.9 | 747.1 |  |
| 18.600 | 359.7 | 0.0018865 | 0.007032 | 1759.80 | 2489.1 | 729.3 |  |
| 18.800 | 360.6 | 0.0019043 | 0.006866 | 1768.90 | 2479.8 | 710.9 |  |
| 19.000 | 361.4 | 0.0019231 | 0.006700 | 1778.20 | 2470.1 | 691.9 |  |
| 19.200 | 362.3 | 0.0019430 | 0.006534 | 1787.70 | 2459.8 | 672.1 |  |
| 19.400 | 363.2 | 0.0019642 | 0.006369 | 1797.50 | 2449.1 | 651.6 |  |
| 19.600 | 364.0 | 0.0019869 | 0.006204 | 1807.50 | 2437.8 | 630.3 |
| 19.800 | 364.9 | 0.0020110 | 0.006039 | 1817.90 | 2426.1 | 608.2 |
| 20.000 | 365.7 | 0.0020380 | 0.006873 | 1828.80 | 2413.8 | 585.0 |
| 20.200 | 366.5 | 0.0020660 | 0.005706 | 1840.10 | 2400.9 | 560.8 |
| 20.400 | 367.4 | 0.0020980 | 0.005537 | 1851.90 | 2387.3 | 535.4 |
| 20.600 | 368.2 | 0.0021340 | 0.005365 | 1864.50 | 2372.8 | 508.3 |
| 20.800 | 369.0 | 0.0021730 | 0.005189 | 1877.90 | 2357.2 | 479.3 |
| 21.000 | 369.8 | 0.0022180 | 0.005006 | 1892.20 | 2340.2 | 448.0 |
| 21.200 | 370.60 | 0.0022680 | 0.004780 | 1907.60 | 2321.3 | 413.7 |
| 21.400 | 371.40 | 0.0023270 | 0.004609 | 1924.70 | 2299.8 | 375.1 |
| 21.600 | 372.2 | 0.0024080 | 0.004382 | 1946.00 | 2274.2 | 328.2 |
| 21.800 | 372.9 | 0.0025100 | 0.004116 | 1971.00 | 2241.6 | 270.6 |
| 22.000 | 373.7 | 0.0026750 | 0.003757 | 2007.70 | 2192.5 | 184.8 |

Table A6. Specific volumes and specific enthalpies of water at various temperatures and pressures.

| T °C | m3/kg | i kJ/kg |  |  |  |  |  | m3/kg |  |  |  | i kJ/kg |  |  |  | m3/kg |  |  |  | i kJ/kg |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | р = 0.1MPa |  |  |  |  |  |  | р = 0.2 MPa |  |  |  |  |  |  |  | р = 0.3 MPa |  |  |  |  |  |  |
| 0 | 0.0010002 |  |  |  | 0.0 |  |  | 0.0010001 |  |  |  | 0.2 |  |  |  | 0.0010001 |  |  |  | 0.3 |  |  |
| 10 | 0.0010003 |  |  |  | 42.1 |  |  | 0.0010002 |  |  |  | 42.2 |  |  |  | 0.0010001 |  |  |  | 42.3 |  |  |
| 20 | 0.0010017 |  |  |  | 84.0 |  |  | 0.0010016 |  |  |  | 84.0 |  |  |  | 0.0010016 |  |  |  | 84.1 |  |  |
| 30 | 0.0010043 |  |  |  | 125.8 |  |  | 0.0010042 |  |  |  | 125.8 |  |  |  | 0.0010042 |  |  |  | 125.9 |  |  |
| 40 | 0.0010078 |  |  |  | 167.5 |  |  | 0.0010077 |  |  |  | 167.6 |  |  |  | 0.0010077 |  |  |  | 167.7 |  |  |
| 50 | 0.0010121 |  |  |  | 209.3 |  |  | 0.0010120 |  |  |  | 209.4 |  |  |  | 0.0010120 |  |  |  | 209.5 |  |  |
| 60 | 0.0010171 |  |  |  | 251.2 |  |  | 0.0010171 |  |  |  | 251.2 |  |  |  | 0.0010170 |  |  |  | 251.3 |  |  |
| 70 | 0.0010228 |  |  |  | 293.0 |  |  | 0.0010228 |  |  |  | 293.1 |  |  |  | 0.0010227 |  |  |  | 293.2 |  |  |
| 80 | 0.0010292 |  |  |  | 335.0 |  |  | 0.0010291 |  |  |  | 335.0 |  |  |  | 0.0010291 |  |  |  | 335.1 |  |  |
| 90 | 0.0010361 |  |  |  | 377.0 |  |  | 0.0010361 |  |  |  | 377.0 |  |  |  | 0.0010360 |  |  |  | 377.1 |  |  |
| 100 | - |  |  |  | - |  |  | 0.0010437 |  |  |  | 419.1 |  |  |  | 0.0010436 |  |  |  | 419.2 |  |  |
| 110 | - |  |  |  | - |  |  | 0.0010518 |  |  |  | 461.4 |  |  |  | 0.0010518 |  |  |  | 461.4 |  |  |
| 120 | - |  |  |  | - |  |  | 0.0010606 |  |  |  | 503.7 |  |  |  | 0.0010606 |  |  |  | 503.8 |  |  |
| 130 | - |  |  |  | - |  |  |  |  |  |  |  |  |  |  | 0.0010700 |  |  |  | 546.3 |  |  |
|  | р = 0.4 MPa |  |  |  |  |  |  | р = 0.6 MPa |  |  |  |  |  |  |  | р = 0.8 MPa |  |  |  |  |  |  |
| 0 | 0.0010000 |  |  |  | 0.4 |  |  | 0.0009999 |  |  |  | 0.6 |  |  |  | 0.0009998 |  |  |  | 0.8 |  |  |
| 10 | 0.0010001 |  |  |  | 42.4 |  |  | 0.0010000 |  |  |  | 42.6 |  |  |  | 0.0009999 |  |  |  | 42.8 |  |  |
| 20 | 0.0010015 |  |  |  | 84.2 |  |  | 0.0010014 |  |  |  | 84.4 |  |  |  | 0.0010014 |  |  |  | 84.6 |  |  |
| 30 | 0.0010041 |  |  |  | 126.0 |  |  | 0.0010040 |  |  |  | 126.2 |  |  |  | 0.0010040 |  |  |  | 126.4 |  |  |
| 40 | 0.0010076 |  |  |  | 167.8 |  |  | 0.0010075 |  |  |  | ;168.0 |  |  |  | 0.0010075 |  |  |  | 168.2 |  |  |
| 50 | 0.0010119 |  |  |  | 209.6 |  |  | 0.0010118 |  |  |  | 209.8 |  |  |  | 0.0010118 |  |  |  | 209.9 |  |  |
| 60 | 0.0010170 |  |  |  | 251.4 |  |  | 0.0010169 |  |  |  | 251.6 |  |  |  | 0.0010168 |  |  |  | 251.7 |  |  |
| 70 | 0.0010227 |  |  |  | 293.3 |  |  | 0.0010226 |  |  |  | 293.4 |  |  |  | 0.0010225 |  |  |  | 293.6 |  |  |
| 80 | 0.0010290 |  |  |  | 335.2 |  |  | 0.0010289 |  |  |  | 335.4 |  |  |  | 0.0010288 |  |  |  | 335.5 |  |  |
| 90 | 0.0010360 |  |  |  | 377.2 |  |  | 0.0010359 |  |  |  | 377.3 |  |  |  | 0.0010358 |  |  |  | 377.5 |  |  |
| 100 | 0.0010436 |  |  |  | 419.3 |  |  | 0.0010434 |  |  |  | 419.4 |  |  |  | 0.0010433 |  |  |  | 419.6 |  |  |
| 110 | 0.0010517 |  |  |  | 461.5 |  |  | 0.0010516 |  |  |  | 461.6 |  |  |  | 0.0010515 |  |  |  | 461.8 |  |  |
| 120 | 0.0010605 |  |  |  | 503.9 |  |  | 0.0010604 |  |  |  | 504.0 |  |  |  | 0.0010603 |  |  |  | 504.1 |  |  |
| 130 | 0.0010699 |  |  |  | 546.4 |  |  | 0.0010698 |  |  |  | 546.5 |  |  |  | 0.0010697 |  |  |  | 546.7 |  |  |
| 140 | 0.0010800 |  |  |  | 589. 1 |  |  | 0.0010799 |  |  |  | 589.3 |  |  |  | 0.0010798 |  |  |  | 589.4 |  |  |
| 150 | - |  |  |  | - |  |  | 0.0010907 |  |  |  | 632.2 |  |  |  | 0.0010906 |  |  |  | 632.4 |  |  |
| 160 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0011021 |  |  |  | 675.6 |  |  |
| 170 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0011144 |  |  |  | 719.1 |  |  |
|  | р = 1.0 MPa |  |  |  |  |  |  | р = 1.5 MPa |  |  |  |  |  |  |  | р = 2.0 MPa |  |  |  |  |  |  |
| 0 | 0.0009997 |  |  |  | 1.0 |  |  | 0.0009995 |  |  |  | 1.5 |  |  |  | 0.0009992 |  |  |  | 2.0 |  |  |
| 10 | 0.0009998 |  |  |  | 43.0 |  |  | 0.0009995 |  |  |  | 43.5 |  |  |  | 0.0009993 |  |  |  | 43.9 |  |  |
| 20 | 0.0010013 |  |  |  | 84.8 |  |  | 0.0010010 |  |  |  | 85.3 |  |  |  | 0.0010008 |  |  |  | 85.7 |  |  |
| 30 | 0.0010039 |  |  |  | 126.6 |  |  | 0.0010036 |  |  |  | 127.0 |  |  |  | 0.0010034 |  |  |  | 127.5 |  |  |
| 40 | 0.0010074 |  |  |  | 168.3 |  |  | 0.0010071 |  |  |  | 168.8 |  |  |  | 0.0010069 |  |  |  | 169.2 |  |  |
| 50 | 0.0010117 |  |  |  | 210.1 |  |  | 0.0010114 |  |  |  | 210.6 |  |  |  | 0.0010112 |  |  |  | 211.0 |  |  |
| 60 | 0.0010167 |  |  |  | 251.9 |  |  | 0.0010165 |  |  |  | 252.3 |  |  |  | 0.0010162 |  |  |  | 252.7 |  |  |
| 70 | 0.0010224 |  |  |  | 293.8 |  |  | 0.0010222 |  |  |  | 294.2 |  |  |  | 0.0010219 |  |  |  | 294.6 |  |  |
| 80 | 0.0010287 |  |  |  | 335.7 |  |  | 0.0010285 |  |  |  | 336.1 |  |  |  | 0.0010282 |  |  |  | 336.5 |  |  |
| 90 | 0.0010357 |  |  |  | 377.7 |  |  | 0.0010354 |  |  |  | 378.0 |  |  |  | 0.0010352 |  |  |  | 378.4 |  |  |
| 100 | 0.0010432 |  |  |  | 419.7 |  |  | 0.0010430 |  |  |  | 420.1 |  |  |  | 0.0010427 |  |  |  | 420.5 |  |  |
| 110 | 0.0010514 |  |  |  | 461.9 |  |  | 0.0010511 |  |  |  | 462.3 |  |  |  | 0.0010508 |  |  |  | 462.7 |  |  |
| 120 | 0.0010602 |  |  |  | 504.3 |  |  | 0.0010599 |  |  |  | 504.6 |  |  |  | 0.0010596 |  |  |  | 505.0 |  |  |
| 130 | 0.0010696 |  |  |  | 546.8 |  |  | 0.0010693 |  |  |  | 547.1 |  |  |  | 0.0010690 |  |  |  | 547.5 |  |  |
| 140 | 0.0010796 |  |  |  | 589.5 |  |  | 0.0010793 |  |  |  | 589.8 |  |  |  | 0.0010790 |  |  |  | 590.2 |  |  |
| 150 | 0.0010904 |  |  |  | 632.5 |  |  | 0.0010901 |  |  |  | 632.8 |  |  |  | 0.0010897 |  |  |  | 633.1 |  |  |
| 160 | 0.0011019 |  |  |  | 675.7 |  |  | 0.0011016 |  |  |  | 676.0 |  |  |  | 10.0011012 |  |  |  | 676.3 |  |  |
| 170 | 0.0011143 |  |  |  | 719.2 1 |  |  | 0.0011139 |  |  |  | 719.5 |  |  |  | 0.0011135 |  |  |  | 719.8 |  |  |
| 180 | - |  |  |  | - |  |  | 0.0011271 |  |  |  | 763.4 |  |  |  | 0.0011266 |  |  |  | 763.6 |  |  |
| 190 | - |  |  |  | - |  |  | 0.0011413 |  |  |  | 807.6 |  |  |  | 0.0011408 |  |  |  | 807.9 |  |  |
| 200 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0011560 |  |  |  | 852.6 |  |  |
| 210 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0011725 |  |  |  | 897.8 |  |  |
|  | р = 3.0 MPa |  |  |  |  |  |  | р = 4.0 MPa |  |  |  |  |  |  |  | р = 5.0 MPa |  |  |  |  |  |  |
| 0 | 0.0009987 |  |  |  | 3.0 |  |  | 0.0009982 |  |  |  | 4.0 |  |  |  | 0.0009977 |  |  |  | 5.1 |  |  |
| 10 | 0.0009988 |  |  |  | 44.9 |  |  | 0.0009984 |  |  |  | 45.9 |  |  |  | 0.0009979 |  |  |  | 46.9 |  |  |
| 20 | 0.0010004 |  |  |  | 86.7 |  |  | 0.0009999 |  |  |  | 87.6 |  |  |  | 0.0009995 |  |  |  | 88.6 |  |  |
| 30 | 0.0010030 |  |  |  | 128.4 |  |  | 0.0010025 |  |  |  | 129.3 |  |  |  | 0.0010021 |  |  |  | 130.2 |  |  |
| 40 | 0.0010065 |  |  |  | Ι70.Ι |  |  | 0.0010060 |  |  |  | 171.0 |  |  |  | 0.0010056 |  |  |  | 171.9 |  |  |
| 50 | 0.0010108 |  |  |  | 211.8 |  |  | 0.0010103 |  |  |  | 212.7 |  |  |  | 0.0010099 |  |  |  | 213.6 |  |  |
| 60 | 0.0010158 |  |  |  | 253.6 |  |  | 0.0010153 |  |  |  | 254.4 |  |  |  | 0.0010149 |  |  |  | 255.3 |  |  |
| 70 | 0.0010215 |  |  |  | 295.4 |  |  | 0.0010210 |  |  |  | 296.2 |  |  |  | 0.0010205 |  |  |  | 297.0 |  |  |
| 80 | 0.0010278 |  |  |  | 337.3 |  |  | 0.0010273 |  |  |  | 338.1 |  |  |  | 0.0010268 |  |  |  | 338.8 |  |  |
| 90 | 0.0010347 |  |  |  | 379.2 |  |  | 0.0010342 |  |  |  | 380.0 |  |  |  | 0.0010337 |  |  |  | 380.7 |  |  |
| 100 | 0.0010422 |  |  |  | 421.2 |  |  | 0.0010417 |  |  |  | 422.0 |  |  |  | 0.0010412 |  |  |  | 422.7 |  |  |
| 110 | 0.0010503 |  |  |  | 463.4 |  |  | 0.0010498 |  |  |  | 464.1 |  |  |  | 0.0010492 |  |  |  | 464.8 |  |  |
| 120 | 0.0010590 |  |  |  | 505.7 |  |  | 0.0010584 |  |  |  | 506.4 |  |  |  | 0.0010579 |  |  |  | 507.1 |  |  |
| 130 | 0.0010684 |  |  |  | 548.2 |  |  | 0.0010677 |  |  |  | 548.8 |  |  |  | 0.0010671 |  |  |  | 549.5 |  |  |
| 140 | 0.0010783 |  |  |  | 590.8 |  |  | 0.0010777 |  |  |  | 591.5 |  |  |  | 0.0010771 |  |  |  | 592.1 |  |  |
| 150 | 0.0010890 |  |  |  | 633.7 |  |  | 0.0010883 |  |  |  | 634.3 |  |  |  | 0.0010877 |  |  |  | 635.0 |  |  |
| 160 | 0.0011005 |  |  |  | 676.9 |  |  | 0.0010997 |  |  |  | 677.5 |  |  |  | 0.0010990 |  |  |  | 678.0 |  |  |
| 170 | 0.0011127 |  |  |  | 720.3 |  |  | 0.0011119 |  |  |  | 720.9 |  |  |  | 0.0011111 |  |  |  | 721.4 |  |  |
| 180 | 0.0011258 |  |  |  | 764.1 |  |  | 0.0011249 |  |  |  | 764.6 |  |  |  | 0.0011241 |  |  |  | 765.2 |  |  |
| 190 | 0.0011399 |  |  |  | 808.3 |  |  | 0.0011389 |  |  |  | 808.8 |  |  |  | 0.0011380 |  |  |  | 809.3 |  |  |
| 200 | 0.0011550 |  |  |  | 853.0 |  |  | 0.0011540 |  |  |  | 853.4 |  |  |  | 0.0011530 |  |  |  | 853.8 |  |  |
| 210 | 0.0011714 |  |  |  | 898.1 |  |  | 0.0011702 |  |  |  | 898.5 |  |  |  | 0.0011691 |  |  |  | 898.8 |  |  |
| 220 | 0.0011891 |  |  |  | 943.9 |  |  | 0.0011878 |  |  |  | 944.2 |  |  |  | 0.0011866 |  |  |  | 944.4 |  |  |
| 230 | 0.0012084 |  |  |  | 990.3 |  |  | 0.0012070 |  |  |  | 990.5 |  |  |  | 0.0012056 |  |  |  | 990.7 |  |  |
| 240 | - |  |  |  | - |  |  | 0.0012280 |  |  |  | 1037.7 |  |  |  | 0.0012264 |  |  |  | 1037.8 |  |  |
| 250 | - |  |  |  | - |  |  | 0.0012512 |  |  |  | 1085.8 |  |  |  | 0.0012494 |  |  |  | 1085.8 |  |  |
| 260 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0012750 |  |  |  | 1135.0 |  |  |
|  | р = 6.0 MPa |  |  |  |  |  |  | р = 7.0 MPa |  |  |  |  |  |  |  | р = 8.0 MPa |  |  |  |  |  |  |
| 0 | 0.0009972 |  |  |  | 6.1 |  |  | 0.0009967 |  |  |  | 7.1 |  |  |  | 0.0009962 |  |  |  | 8.1 |  |  |
| 10 | 0.0009974 |  |  |  | 47.8 |  |  | 0.0009970 |  |  |  | 48.8 |  |  |  | 0.0009965 |  |  |  | 49.8 |  |  |
| 20 | 0.0009990 |  |  |  | 89.5 |  |  | 0.0009986 |  |  |  | 90.4 |  |  |  | 0.0009981 |  |  |  | 91.4 |  |  |
| 30 | 0.0010016 |  |  |  | 131.1 |  |  | 0.0010012 |  |  |  | 132.0 |  |  |  | 0.0010008 |  |  |  | 132.9 |  |  |
| 40 | 0.0010051 |  |  |  | 172.7 |  |  | 0.0010047 |  |  |  | 173.6 |  |  |  | 0.0010043 |  |  |  | 174.5 |  |  |
| 50 | 0.0010094 |  |  |  | 214.4 |  |  | 0.0010090 |  |  |  | 215.3 |  |  |  | 0.0010086 |  |  |  | 216.1 |  |  |
| 60 | 0.0010144 |  |  |  | 256.1 |  |  | 0.0010140 |  |  |  | 256.9 |  |  |  | 0.0010135 |  |  |  | 257.8 |  |  |
| 70 | 0.0010201 |  |  |  | 297.8 |  |  | 0.0010196 |  |  |  | 298.7 |  |  |  | 0.0010192 |  |  |  | 299.5 |  |  |
| 80 | 0.0010263 |  |  |  | 339.6 |  |  | 0.0010259 |  |  |  | 340.4 |  |  |  | 0.0010254 |  |  |  | 341.2 |  |  |
| 90 | 0.0010332 |  |  |  | 381.5 |  |  | 0.0010327 |  |  |  | 382.3 |  |  |  | 0.0010322 |  |  |  | 383.1 |  |  |
| 100 | 0.0010406 |  |  |  | 423.5 |  |  | 0.0010401 |  |  |  | 424.2 |  |  |  | 0.0010396 |  |  |  | 425.0 |  |  |
| 110 | 0.0010487 |  |  |  | 465.6 |  |  | 0.0010481 |  |  |  | 466.3 |  |  |  | 0.0010476 |  |  |  | 467.0 |  |  |
| 120 | 0.0010573 |  |  |  | 507.8 |  |  | 0.0010567 |  |  |  | 508.5 |  |  |  | 0.0010562 |  |  |  | 509.2 |  |  |
| 130 | 0.0010665 |  |  |  | 550.2 |  |  | 0.0010660 |  |  |  | 550.9 |  |  |  | 0.0010654 |  |  |  | 551.6 |  |  |
| 140 | 0.0010764 |  |  |  | 592.8 |  |  | 0.0010758 |  |  |  | 593.4 |  |  |  | 0.0010752 |  |  |  | 594.1 |  |  |
| 150 | 0.0010870 |  |  |  | 635.6 |  |  | 0.0010863 |  |  |  | 636.2 |  |  |  | 0.0010856 |  |  |  | 636.8 |  |  |
| 160 | 0.0010983 |  |  |  | 678.6 |  |  | 0.0010976 |  |  |  | 679.2 |  |  |  | 1 0.00 10968 |  |  |  | 679.8 |  |  |
|  | р = 6.0 MPa |  |  |  |  |  |  | р = 7.0 ΜΠа |  |  |  |  |  |  |  | р = 8.0 MPa |  |  |  |  |  |  |
| 170 | 0.0011103 |  |  |  | 722.0 |  |  | 0.0011096 |  |  |  | 722.6 |  |  |  | 0.0011088 |  |  |  | 723.1 |  |  |
| 180 | 0.0011232 |  |  |  | 765.7 |  |  | 0.0011224 |  |  |  | 766.2 |  |  |  | 0.0011216 |  |  |  | 766.7 |  |  |
| 190 | 0.0011371 |  |  |  | 809.7 |  |  | 0.0011362 |  |  |  | 810.2 |  |  |  | 0.0011353 |  |  |  | 810.7 |  |  |
| 200 | 0.0011519 |  |  |  | 854.2 |  |  | 0.0011510 |  |  |  | 854.6 |  |  |  | 0.0011500 |  |  |  | 855.1 |  |  |
| 210 | 0.0011680 |  |  |  | 899.2 |  |  | 0.0011669 |  |  |  | 899.6 |  |  |  | 0.0011658 |  |  |  | 899.9 |  |  |
| 220 | 0.0011853 |  |  |  | 944.7 |  |  | 0.0011841 |  |  |  | 945.0 |  |  |  | 0.0011829 |  |  |  | 945.3 |  |  |
| 230 | 0.0012042 |  |  |  | 990.9 |  |  | 0.0012028 |  |  |  | 991.1 |  |  |  | 0.0012015 |  |  |  | 991.4 |  |  |
| 240 | 0.0012249 |  |  |  | 1037.9 |  |  | 0.0012233 |  |  |  | 1038 |  |  |  | 0.0012218 |  |  |  | 1038.2 |  |  |
| 250 | 0.0012476 |  |  |  | 1085.8 |  |  | 0.0012458 |  |  |  | 1085.8 |  |  |  | 0.001244 |  |  |  | 1085.8 |  |  |
| 260 | 0.0012729 |  |  |  | 1134.8 |  |  | 0.0012708 |  |  |  | 1134.7 |  |  |  | 0.0012687 |  |  |  | 1134.6 |  |  |
| 270 | 0.0013013 |  |  |  | 1185.2 |  |  | 0.0012988 |  |  |  | 1184.9 |  |  |  | 0.0012964 |  |  |  | 1184.6 |  |  |
| 280 | - |  |  |  | - |  |  | 0.0013307 |  |  |  | 1236.7 |  |  |  | 0.0013277 |  |  |  | 1236.2 |  |  |
| 290 | - |  |  |  | - |  |  | - |  |  |  | - |  |  |  | 0.0013639 |  |  |  | 1289.8 |  |  |
|  | р = 9.0 MPa |  |  |  |  |  |  | р = 10.0 MPa |  |  |  |  |  |  |  | р = 11.0 MPa |  |  |  |  |  |  |
| 0 | 0.0009958 |  |  |  | 9.1 |  |  | 0.0009953 |  |  |  | 10.1 |  |  |  | 0.0009948 |  |  |  | 11.1 |  |  |
| 10 | 0.0009960 |  |  |  | 50.7 |  |  | 0.0009956 |  |  |  | 51.7 |  |  |  | 0.0009951 |  |  |  | 52.7 |  |  |
| 20 | 0.0009977 |  |  |  | 92.3 |  |  | 0.0009972 |  |  |  | 93.2 |  |  |  | 0.0009968 |  |  |  | 94.2 |  |  |
| 30 | 0.0010003 |  |  |  | 133.8 |  |  | 0.0009999 |  |  |  | 134.7 |  |  |  | 0.0009995 |  |  |  | 135.7 |  |  |
| 40 | 0.0010038 |  |  |  | 175.4 |  |  | 0.0010034 |  |  |  | 176.3 |  |  |  | 0.0010030 |  |  |  | 177.2 |  |  |
| 50 | 0.0010081 |  |  |  | 217.0 |  |  | 0.0010077 |  |  |  | 217.8 |  |  |  | 0.0010073 |  |  |  | 218.7 |  |  |
| 60 | 0.0010131 |  |  |  | 258.6 |  |  | 0.0010126 |  |  |  | 259.4 |  |  |  | 0.0010122 |  |  |  | 260.3 |  |  |
| 70 | 0.0010187 |  |  |  | 300.3 |  |  | 0.0010182 |  |  |  | 301.1 |  |  |  | 0.0010178 |  |  |  | 301.9 |  |  |
| 80 | 0.0010249 |  |  |  | 342.0 |  |  | 0.0010244 |  |  |  | 342.8 |  |  |  | 0.0010240 |  |  |  | 343.6 |  |  |
| 90 | 0.0010317 |  |  |  | 383.8 |  |  | 0.0010312 |  |  |  | 384.6 |  |  |  | 0.0010308 |  |  |  | 385.4 |  |  |
| 100 | 0.0010391 |  |  |  | 425.8 |  |  | 0.0010386 |  |  |  | 426.5 |  |  |  | 0.0010381 |  |  |  | 427.2 |  |  |
| 110 | 0.0010471 |  |  |  | 467.8 |  |  | 0.0010465 |  |  |  | 468.5 |  |  |  | 0.0010460 |  |  |  | 469.2 |  |  |
| 120 | 0.0010556 |  |  |  | 509.9 |  |  | 0.0010551 |  |  |  | 510.6 |  |  |  | 0.0010545 |  |  |  | 511.3 |  |  |
| 130 | 0.0010648 |  |  |  | 552.2 |  |  | 0.0010642 |  |  |  | 552.9 |  |  |  | 0.0010636 |  |  |  | 553.6 |  |  |
| 140 | 0.0010745 |  |  |  | 594.7 |  |  | 0.0010739 |  |  |  | 595.4 |  |  |  | 0.0010733 |  |  |  | 596.1 |  |  |
| 150 | 0.0010850 |  |  |  | 637.5 |  |  | 0.0010843 |  |  |  | 638.1 |  |  |  | 0.0010837 |  |  |  | 638.7 |  |  |
| 160 | 0.0010961 |  |  |  | 680.4 |  |  | 0.0010954 |  |  |  | 681.0 |  |  |  | 0.0010947 |  |  |  | 681.6 |  |  |
| 170 | 0.0011080 |  |  |  | 723.7 |  |  | 0.0011072 |  |  |  | 724.2 |  |  |  | 0.0011065 |  |  |  | 724.8 |  |  |
| 180 | 0.0011207 |  |  |  | 767.2 |  |  | 0.0011199 |  |  |  | 767.8 |  |  |  | 0.0011191 |  |  |  | 768.3 |  |  |
| 190 | 0.0011344 |  |  |  | 811.2 |  |  | 0.0011335 |  |  |  | 811.6 |  |  |  | 0.0011326 |  |  |  | 812.1 |  |  |
| 200 | 0.0011490 |  |  |  | 855.5 |  |  | 0.0011480 |  |  |  | 855.9 |  |  |  | 0.0011470 |  |  |  | 856.4 |  |  |
| 210 | 0.0011647 |  |  |  | 900.3 |  |  | 0.0011636 |  |  |  | 900.7 |  |  |  | 0.0011626 |  |  |  | 901.1 |  |  |
| 220 | 0.0011817 |  |  |  | 945.6 |  |  | 0.0011805 |  |  |  | 946.0 |  |  |  | 0.0011793 |  |  |  | 946.3 |  |  |
| 230 | 0.0012001 |  |  |  | 991.6 |  |  | 0.0011988 |  |  |  | 991.8 |  |  |  | 0.0011975 |  |  |  | 992.1 |  |  |
| 240 | 0.0012202 |  |  |  | 1038.3 |  |  | 0.0012188 |  |  |  | 1038.4 |  |  |  | 0.0012173 |  |  |  | 1038.6 |  |  |
| 250 | 0.0012423 |  |  | 1085.9 |  |  | 0.0012406 |  |  |  | 1085.9 |  |  |  | 0.0012389 |  |  |  | 1085.9 |  |  |
| 260 | 0.0012667 |  |  | 1134.4 |  |  | 0.0012648 |  |  |  | 1134.3 |  |  |  | 0.0012628 |  |  |  | 1134.3 |  |  |
| 270 | 0.0012940 |  |  | 1184.3 |  |  | 0.0012917 |  |  |  | 1184.0 |  |  |  | 0.0012894 |  |  |  | 1183.8 |  |  |
| 280 | 0.0013249 |  |  | 1235.6 |  |  | 0.0013221 |  |  |  | 1235.2 |  |  |  | 0.0013194 |  |  |  | 1234.7 |  |  |
| 290 | 0.0013604 |  |  | 1289.0 |  |  | 0.0013570 |  |  |  | 1288.2 |  |  |  | 0.0013536 |  |  |  | 1287.5 |  |  |
| 300 | 0.0014022 |  |  | 1344.9 |  |  | 0.0013978 |  |  |  | 1343.7 |  |  |  | 0.0013936 |  |  |  | 1342.6 |  |  |
| 310 | - |  |  | - |  |  | 0.0014472 |  |  |  | 1402.6 |  |  |  | 0.0014416 |  |  |  | 1400.9 |  |  |
|  | р = 12.0 MPa |  |  |  |  |  | р = 13.0 MPa. |  |  |  |  |  |  |  | р = 14.0 MPa |  |  |  |  |  |  |
| 0 | 0.0009943 |  |  | 12.1 |  |  | 0.0009938 |  |  |  | 13.1 |  |  |  | 0.0009933 |  |  |  | 14.1 |  |  |
| 10 | 0.0009947 |  |  | 53.6 |  |  | 0.0009942 |  |  |  | 54.6 |  |  |  | 0.0009938 |  |  |  | 55.6 |  |  |
| 20 | 0.0009964 |  |  | 95.1 |  |  | 0.0009959 |  |  |  | 96.0 |  |  |  | 0.0009955 |  |  |  | 97 |  |  |
| 30 | 0.0009991 |  |  | 136.6 |  |  | 0.0009986 |  |  |  | 137.4 |  |  |  | 0.0009982 |  |  |  | 138.4 |  |  |
| 40 | 0.0010026 |  |  | 178.1 |  |  | 0.0010021 |  |  |  | 178.9 |  |  |  | 0.0010017 |  |  |  | 179.8 |  |  |
| 50 | 0.0010068 |  |  | 219.6 |  |  | 0.0010064 |  |  |  | 220.4 |  |  |  | 0.001006 |  |  |  | 221.3 |  |  |
| 60 | 0.0010118 |  |  | 261.1 |  |  | 0.0010113 |  |  |  | 262.0 |  |  |  | 0.0010109 |  |  |  | 262.8 |  |  |
| 70 | 0.0010174 |  |  | 302.7 |  |  | 0.0010169 |  |  |  | 303.6 |  |  |  | 0.0010164 |  |  |  | 304.4 |  |  |
| 80 | 0.0010235 |  |  | 344.4 |  |  | 0.0010231 |  |  |  | 345.2 |  |  |  | 0.0010226 |  |  |  | 346.0 |  |  |
| 90 | 0.0010303 |  |  | 386.2 |  |  | 0.0010298 |  |  |  | 386.9 |  |  |  | 0.0010293 |  |  |  | 387.7 |  |  |
| 100 | 0.0010376 |  |  | 428.0 |  |  | 0.0010371 |  |  |  | 428.8 |  |  |  | 0.0010366 |  |  |  | 429.5 |  |  |
| 110 | 0.0010455 |  |  | 470.0 |  |  | 0.0010450 |  |  |  | 470.7 |  |  |  | 0.0010444 |  |  |  | 471.4 |  |  |
| 120 | 0.001054 |  |  | 512.0 |  |  | 0.0010534 |  |  |  | 512.8 |  |  |  | 0.0010529 |  |  |  | 513.5 |  |  |
| 130 | 0.001063 |  |  | 554.3 |  |  | 0.0010624 |  |  |  | 555.0 |  |  |  | 0.0010619 |  |  |  | 555.7 |  |  |
| 140 | 0.0010727 |  |  | 596.7 |  |  | 0.0010721 |  |  |  | 597.4 |  |  |  | 0.0010715 |  |  |  | 598.0 |  |  |
| 150 | 0.001083 |  |  | 639.3 |  |  | 0.0010824 |  |  |  | 640.0 |  |  |  | 0.0010817 |  |  |  | 640.6 |  |  |
| 160 | 0.001094 |  |  | 682.2 |  |  | 0.0010933 |  |  |  | 682.8 |  |  |  | 0.0010926 |  |  |  | 683.4 |  |  |
| 170 | 0.0011058 |  |  | 725.4 |  |  | 0.0011050 |  |  |  | 725.9 |  |  |  | 0.0011043 |  |  |  | 726.5 |  |  |
| 180 | 0.0011183 |  |  | 768.8 |  |  | 0.0011175 |  |  |  | 769.4 |  |  |  | 0.0011167 |  |  |  | 769.9 |  |  |
| 190 | 0.0011317 |  |  | 812.6 |  |  | 0.0011308 |  |  |  | 813.1 |  |  |  | 0.00113 |  |  |  | 813.6 |  |  |
| 200 | 0.0011461 |  |  | 856.8 |  |  | 0.0011451 |  |  |  | 857.2 |  |  |  | 0.0011442 |  |  |  | 857.7 |  |  |
| 210 | 0.0011615 |  |  | 901.4 |  |  | 0.0011605 |  |  |  | 901.8 |  |  |  | 0.0011594 |  |  |  | 902.2 |  |  |
| 220 | 0.0011782 |  |  | 946.6 |  |  | 0.0011770 |  |  |  | 946.9 |  |  |  | 0.0011759 |  |  |  | 947.2 |  |  |
| 230 | 0.0011962 |  |  | 992.3 |  |  | 0.0011949 |  |  |  | 992.6 |  |  |  | 0.0011936 |  |  |  | 992.8 |  |  |
| 240 | 0.0012158 |  |  | 1038.8 |  |  | 0.0012144 |  |  |  | 1038.9 |  |  |  | 0.0012129 |  |  |  | 1039.1 |  |  |
| 250 | 0.0012373 |  |  | 1086.0 |  |  | 0.0012356 |  |  |  | 1086.1 |  |  |  | 0.0012340 |  |  |  | 1086.1 |  |  |
| 260 | 0.0012609 |  |  | 1134.2 |  |  | 0.0012590 |  |  |  | 1134.1 |  |  |  | 0.0012572 |  |  |  | 1134.1 |  |  |
| 270 | 0.0012872 |  |  | 1183.5 |  |  | 0.0012850 |  |  |  | 1183.3 |  |  |  | 0.0012828 |  |  |  | 1183.1 |  |  |
| 280 | 0.0013167 |  |  | 1234.3 |  |  | 0.0013141 |  |  |  | 1233.9 |  |  |  | 0.0013115 |  |  |  | 1233.5 |  |  |
| 290 | 0.0013504 |  | 1286.8 |  |  | 0.0013472 |  |  |  | 1286.1 |  |  |  | 0.0013441 |  |  |  | 1285.5 |  |  |  |
| 300 | 0.0013895 |  | 1341.5 |  |  | 0.0013855 |  |  |  | 1340.5 |  |  |  | 0.0013816 |  |  |  | 1339.5 |  |  |  |
| 310 | 0.0014362 |  | 1399.3 |  |  | 0.0014310 |  |  |  | 1397.8 |  |  |  | 0.0014260 |  |  |  | 1396.4 |  |  |  |
| 320 | 0.0014941 |  | 1461.5 |  |  | 0.0014869 |  |  |  | 1459.2 |  |  |  | 0.0014801 |  |  |  | 1457.0 |  |  |  |
| 330 | - |  | - |  |  | 0.0015600 |  |  |  | 1526.9 |  |  |  | 0.0015497 |  |  |  | 1523.5 |  |  |  |
|  | р = 15.0 MPa |  |  |  |  | р = 16.0 MPa |  |  |  |  |  |  |  | р = 17.0 MPa |  |  |  |  |  |  |  |
| 0 | 0.0009928 |  | 15.1 |  |  | 0.0009924 |  |  |  | 16.1 |  |  |  | 0.0009919 |  |  |  | 17.1 |  |  |  |
| 10 | 0.0009933 |  | 56.5 |  |  | 0.0009928 |  |  |  | 57.5 |  |  |  | 0.0009924 |  |  |  | 58.4 |  |  |  |
| 20 | 0.0009950 |  | 97.9 |  |  | 0.0009946 |  |  |  | 98.8 |  |  |  | 0.0009942 |  |  |  | 99.7 |  |  |  |
| 30 | 0.0009978 |  | 139.3 |  |  | 0.0009973 |  |  |  | 140.2 |  |  |  | 0.0009969 |  |  |  | 141.1 |  |  |  |
| 40 | 0.0010013 |  | 180.7 |  |  | 0.0010008 |  |  |  | 181.6 |  |  |  | 0.0010004 |  |  |  | 182.4 |  |  |  |
| 50 | 0.0010055 |  | 222.1 |  |  | 0.0010051 |  |  |  | 223.0 |  |  |  | 0.0010047 |  |  |  | 223.8 |  |  |  |
| 60 | 0.0010105 |  | 263.6 |  |  | 0.0010100 |  |  |  | 264.5 |  |  |  | 0.0010096 |  |  |  | 265.3 |  |  |  |
| 70 | 0.0010160 |  | 305.2 |  |  | 0.0010156 |  |  |  | 306.0 |  |  |  | 0.0010151 |  |  |  | 306.8 |  |  |  |
| 80 | 0.0010221 |  | 346.8 |  |  | 0.0010217 |  |  |  | 347.6 |  |  |  | 0.0010212 |  |  |  | 348.4 |  |  |  |
| 90 | 0.0010289 |  | 388.5 |  |  | 0.0010284 |  |  |  | 389.3 |  |  |  | 0.0010279 |  |  |  | 390.0 |  |  |  |
| 100 | 0.0010361 |  | 430.3 |  |  | 0.0010356 |  |  |  | 431.0 |  |  |  | 0.0010351 |  |  |  | 431.8 |  |  |  |
| 110 | 0.0010439 |  | 472.2 |  |  | 0.0010434 |  |  |  | 472.9 |  |  |  | 0.0010429 |  |  |  | 473.6 |  |  |  |
| 120 | 0.0010523 |  | 514.2 |  |  | 0.0010518 |  |  |  | 514.9 |  |  |  | 0.0010512 |  |  |  | 515.6 |  |  |  |
| 130 | 0.0010613 |  | 556.4 |  |  | 0.0010607 |  |  |  | 557.0 |  |  |  | 0.0010602 |  |  |  | 557.7 |  |  |  |
| 140 | 0.0010709 |  | 598.7 |  |  | 0.0010703 |  |  |  | 599.4 |  |  |  | 0.0010697 |  |  |  | 600.0 |  |  |  |
| 150 | 0.0010811 |  | 641.3 |  |  | 0.0010804 |  |  |  | 641.9 |  |  |  | 0.0010798 |  |  |  | 642.5 |  |  |  |
| 160 | 0.0010919 |  | 684.0 |  |  | 0.0010912 |  |  |  | 684.6 |  |  |  | 0.0010906 |  |  |  | 685.2 |  |  |  |
| 170 | 0.0011035 |  | 727.1 |  |  | 0.0011028 |  |  |  | 727.7 |  |  |  | 0.0011021 |  |  |  | 728.2 |  |  |  |
| 180 | 0.0011159 |  | 770.4 |  |  | 0.0011151 |  |  |  | 771.0 |  |  |  | 0.0011143 |  |  |  | 771.5 |  |  |  |
| 190 | 0.0011291 |  | 814.1 |  |  | 0.0011282 |  |  |  | 814.6 |  |  |  | 0.0011274 |  |  |  | 815.1 |  |  |  |
| 200 | 0.0011432 |  | 858.1 |  |  | 0.0011423 |  |  |  | 858.6 |  |  |  | 0.0011414 |  |  |  | 859.0 |  |  |  |
| 210 | 0.0011584 |  | 902.6 |  |  | 0.0011574 |  |  |  | 903.0 |  |  |  | 0.0011564 |  |  |  | 903.4 |  |  |  |
| 220 | 0.0011748 |  | 947.6 |  |  | 0.0011736 |  |  |  | 947.9 |  |  |  | 0.0011725 |  |  |  | 948.3 |  |  |  |
|  | р = 15.0 MPa |  |  |  |  | р = 16.0 MPa |  |  |  |  |  |  |  | р = 17.0 MPa |  |  |  |  |  |  |  |
| 230 | 0.0011924 |  | 993.1 |  |  | 0.0011912 |  |  |  | 993.4 |  |  |  | 0.0011899 |  |  |  | 993.7 |  |  |  |
| 240 | 0.0012115 |  | 1039.3 |  |  | 0.0012101 |  |  |  | 1039.5 |  |  |  | 0.0012088 |  |  |  | 1039.7 |  |  |  |
| 250 | 0.0012324 |  | 1086.2 |  |  | 0.0012308 |  |  |  | 1086.3 |  |  |  | 0.0012293 |  |  |  | 1086.4 |  |  |  |
| 260 | 0.0012553 |  | 1134.0 |  |  | 0.0012535 |  |  |  | 1134.0 |  |  |  | 0.0012517 |  |  |  | 1134.0 |  |  |  |
| 270 | 0.0012807 |  | 1182.9 |  |  | 0.0012786 |  |  |  | 1182.8 |  |  |  | 0.0012765 |  |  |  | 1182.6 |  |  |  |
| 280 | 0.0013090 |  | 1233.1 |  |  | 0.0013065 |  |  |  | 1232.8 |  |  |  | 0.0013041 |  |  |  | 1232.4 |  |  |  |
| 290 | 0.0013410 |  | 1284.9 |  |  | 0.0013381 |  |  |  | 1284.3 |  |  |  | 0.0013352 |  |  |  | 1283.8 |  |  |  |
| 300 | 0.0013779 |  | 1338.6 |  |  | 0.0013742 |  |  |  | 1337.7 |  |  |  | 0.0013707 |  |  |  | 1336.9 |  |  |  |
| 310 | 0.0014212 |  | 1395.0 |  |  | 0.0014165 |  |  |  | 1393.7 |  |  |  | 0.0014120 |  |  |  | 1392.4 |  |  |  |
| 320 | 0.0014736 |  | 1455.0 |  |  | 0.0014674 |  |  |  | 1453.0 |  |  |  | 0.0014615 |  |  |  | 1451.2 |  |  |  |
| 330 | 0.0015402 |  | 1520.3 |  |  | 0.0015312 |  |  |  | 1517.3 |  |  |  | 0.0015229 |  |  |  | 1514.6 |  |  |  |
| 340 | 0.0016323 |  | 1594.6 |  |  | 0.0016175 |  |  |  | 1589.6 |  |  |  | 0.0016042 |  |  |  | 1585.0 |  |  |  |
| 350 | - |  | - |  |  | - |  |  |  | - |  |  |  | 0.0017286 |  |  |  | 1668.7 |  |  |  |
|  | р = 18.0 MPa |  |  |  |  | р = 19.0 MPa |  |  |  |  |  |  |  | р = 20.0 MPa |  |  |  |  |  |  |  |
| 0 | 0.0009914 |  | 18.1 |  |  | 0.0009909 |  |  |  | 19.1 |  |  |  | 0.0009904 |  |  |  | 20.1 |  |  |  |
| 10 | 0.0009919 |  | 59.4 |  |  | 0.0009915 |  |  |  | 60.4 |  |  |  | 0.0009910 |  |  |  | 61.3 |  |  |  |
| 20 | 0.0009937 |  | 100.7 |  |  | 0.0009933 |  |  |  | 101.6 |  |  |  | 0.0009929 |  |  |  | 102.5 |  |  |  |
| 30 | 0.0009965 |  | 142.0 |  |  | 0.0009960 |  |  |  | 142.9 |  |  |  | 0.0009956 |  |  |  | 143.8 |  |  |  |
| 40 | 0.0010000 |  | 183.3 |  |  | 0.0009996 |  |  |  | 184.2 |  |  |  | 0.0009992 |  |  |  | 185.1 |  |  |  |
| 50 | 0.0010043 |  | 224.7 |  |  | 0.0010038 |  |  |  | 225.6 |  |  |  | 0.0010034 |  |  |  | 226.4 |  |  |  |
| 60 | 0.0010092 |  | 266.1 |  |  | 0.0010087 |  |  |  | 267.0 |  |  |  | 0.0010083 |  |  |  | 267.8 |  |  |  |
| 70 | 0.0010147 |  | 307.6 |  |  | 0.0010142 |  |  |  | 308.4 |  |  |  | 0.0010138 |  |  |  | 309.3 |  |  |  |
| 80 | 0.0010208 |  | 349.2 |  |  | 0.0010203 |  |  |  | 350.0 |  |  |  | 0.0010199 |  |  |  | 350.8 |  |  |  |
| 90 | 0.0010274 |  | 390.8 |  |  | 0.0010270 |  |  |  | 391.6 |  |  |  | 0.0010265 |  |  |  | 392.4 |  |  |  |
| 100 | 0.0010346 |  | 432.5 |  |  | 0.0010342 |  |  |  | 433.3 |  |  |  | 0.0010337 |  |  |  | 434.0 |  |  |  |
| 110 | 0.0010424 |  | 474.4 |  |  | 0.0010419 |  |  |  | 475.1 |  |  |  | 0.0010414 |  |  |  | 475.8 |  |  |  |
| 120 | 0.0010507 |  | 516.3 |  |  | 0.0010502 |  |  |  | 517.0 |  |  |  | 0.0010496 |  |  |  | 517.7 |  |  |  |
|  | р = 18.0 MPa |  |  |  |  | р = 19.0 MPa |  |  |  |  |  |  |  | р = 20.0 MPa |  |  |  |  |  |  |  |
| 130 | 0.0010596 |  | 558.4 |  |  | 0.001059 |  |  |  | 559.1 |  |  |  | 0.0010585 |  |  |  | 559.8 |  |  |  |
| 140 | 0.0010691 |  | 600.7 |  |  | 0.0010685 |  |  |  | 601.4 |  |  |  | 0.0010679 |  |  |  | 602.0 |  |  |  |
| 150 | 0.0010792 |  | 643.2 |  |  | 0.0010785 |  |  |  | 643.8 |  |  |  | 0.0010779 |  |  |  | 644.4 |  |  |  |
| 160 | 0.0010899 |  | 685.9 |  |  | 0.0010892 |  |  |  | 686.5 |  |  |  | 0.0010886 |  |  |  | 687.1 |  |  |  |
| 170 | 0.0011014 |  | 728.8 |  |  | 0.0011006 |  |  |  | 729.4 |  |  |  | 0.0010999 |  |  |  | 730.0 |  |  |  |
| 180 | 0.0011136 |  | 772.0 |  |  | 0.0011128 |  |  |  | 772.6 |  |  |  | 0.0011120 |  |  |  | 773.1 |  |  |  |
| 190 | 0.0011266 |  | 815.6 |  |  | 0.0011257 |  |  |  | 816.1 |  |  |  | 0.0011249 |  |  |  | 816.6 |  |  |  |
| 200 | 0.0011405 |  | 859.5 |  |  | 0.0011396 |  |  |  | 860.0 |  |  |  | 0.0011387 |  |  |  | 860.4 |  |  |  |
| 210 | 0.0011554 |  | 903.8 |  |  | 0.0011545 |  |  |  | 904.2 |  |  |  | 0.0011534 |  |  |  | 904.7 |  |  |  |
| 220 | 0.0011714 |  | 948.6 |  |  | 0.0011703 |  |  |  | 949.0 |  |  |  | 0.0011693 |  |  |  | 949.3 |  |  |  |
| 230 | 0.0011887 |  | 993.9 |  |  | 0.0011875 |  |  |  | 994.2 |  |  |  | 0.0011863 |  |  |  | 994.5 |  |  |  |
| 240 | 0.0012074 |  | 1039.9 |  |  | 0.0012061 |  |  |  | 1040.1 |  |  |  | 0.0012047 |  |  |  | 1040.3 |  |  |  |
| 250 | 0.0012277 |  | 1086.5 |  |  | 0.0012262 |  |  |  | 1086.7 |  |  |  | 0.0012247 |  |  |  | 1086.8 |  |  |  |
| 260 | 0.0012500 |  | 1134.0 |  |  | 0.0012483 |  |  |  | 1134.0 |  |  |  | 0.0012466 |  |  |  | 1134.1 |  |  |  |
| 270 | 0.0012745 |  | 1182.5 |  |  | 0.0012725 |  |  | 1182.4 |  |  |  | 0.0012706 |  |  |  | 1182.3 |  |  |  |
| 280 | 0.0013017 |  | 1232.1 |  |  | 0.0012994 |  |  | 1231.9 |  |  |  | 0.0012971 |  |  |  | 1231.6 |  |  |  |
| 290 | 0.0013324 |  | 1283.2 |  |  | 0.0013296 |  |  | 1282.8 |  |  |  | 0.0013269 |  |  |  | 1282.3 |  |  |  |
| 300 | 0.0013672 |  | 1336.1 |  |  | 0.0013639 |  |  | 1335.3 |  |  |  | 0.0013606 |  |  |  | 1334.6 |  |  |  |
| 310 | 0.0014077 |  | 1391.3 |  |  | 0.0014035 |  |  | 1390.1 |  |  |  | 0.0013994 |  |  |  | 1389.1 |  |  |  |
| 320 | 0.0014558 |  | 1449.5 |  |  | 0.0014503 |  |  | 1447.9 |  |  |  | 0.0014450 |  |  |  | 1446.3 |  |  |  |
| 330 | 0.0015150 |  | 1512.0 |  |  | 0.0015075 |  |  | 1509.6 |  |  |  | 0.0015003 |  |  |  | 1507.3 |  |  |  |
| 340 | 0.0015920 |  | 1580.9 |  |  | 0.0015807 |  |  | 1577.2 |  |  |  | 0.0015703 |  |  |  | 1573.7 |  |  |  |
| 350 | 0.0017040 |  | 1660.9 |  |  | 0.001683 |  |  | 1654.2 |  |  |  | 0.0016660 |  |  |  | 1648.4 |  |  |  |
| 355 | 0.001790 |  | 1710.2 |  |  | 0.001757 |  |  | 1699.8 |  |  |  | 0.001731 |  |  |  | 1691.4 |  |  |  |
| 360 | - |  | - |  |  | 0.001871 |  |  | 1756.8 |  |  |  | 0.001823 |  |  |  | 1742.0 |  |  |  |
| 365 | - |  | - |  |  | - |  |  | - |  |  |  | 0.001991 |  |  |  | 1813.2 |  |  |  |

Table A7. Specific volumes and specific enthalpies of steam at various temperatures and pressures.

| T °C | m3/kg | i kJ/kg | m3/kg | i kJ/kg | m3/kg | i kJ/kg |
| --- | --- | --- | --- | --- | --- | --- |
|  | р = 0.1 MPa |  | р = 0.15 MPa |  | р = 0.2 MPa |  |
| 100 | 1.69600 | 2676.5 | - | - | - | - |
| 110 | 1.74500 | 2696.7 | - | - | - | - |
| 120 | 1.79300 | 2716.8 | 1.18800 | 2711.7 | - | - |
| 130 | 1.84100 | 2736.8 | 1.22100 | 2732.2 | 0.91040 | 2727.5 |
| 140 | 1.88900 | 2756.6 | 1.25300 | 2752.5 | 0.93520 | 2748.4 |
| 150 | 1.93700 | 2776.4 | 1.28600 | 2772.7 | 0.95980 | 2769.0 |
| 160 | 1.98400 | 2796.2 | 1.31800 | 2792.9 | 0.98420 | 2789.5 |
| 170 | 2.03100 | 2816.0 | 1.34900 | 2812.9 | 1.00800 | 2809.8 |
| 180 | 2.07800 | 2835.7 | 1.38100 | 2832.9 | 1.03200 | 2830. 1 |
| 190 | 2.12500 | 2855.4 | 1.41300 | 2852.8 | 1.05600 | 2850.3 |
| 200 | 2.17200 | 2875.2 | 1.44400 | 2872.8 | 1.08000 | 2870.4 |
| 210 | 2.21900 | 2894.9 | 1.47600 | 2892.7 | 1.10400 | 2890.5 |
| 220 | 2.26600 | 2914.7 | 1.50700 | 2912.6 | 1.12800 | 2910.6 |
| 230 | 2.31300 | 2934.5 | 1.53900 | 2932.6 | 1.15200 | 2930.7 |
| 240 | 2.35900 | 2954.3 | 1.57000 | 2952.6 | 1.17500 | 2950.8 |
| 250 | 2.40600 | 2974.2 | 1.60100 | 2972.5 | 1.19900 | 2970.8 |
| 260 | 2.45300 | 2994.1 | 1.63200 | 2992.5 | 1.22200 | 2990.9 |
| 270 | 2.49900 | 3014.0 | 1.66400 | 3012.5 | 1.24600 | 3011.1 |
| 280 | 2.54600 | 3034.0 | 1.69500 | 3032.6 | 1.26900 | 3031.2 |
| 290 | 2.59200 | 3054.0 | 1.72600 | 3052.7 | 1.29300 | 3051.4 |
| 300 | 2.63900 | 3074.1 | 1.75700 | 3072.9 | 1.31600 | 3071.6 |
| 310 | 2.68500 | 3094.3 | 1.78800 | 3093.1 | 1.34000 | 3091.9 |
| 320 | 2.73200 | 3114.4 | 1.81900 | 3113.3 | 1.36300 | 3112.2 |
| 330 | 2.77800 | 3134.7 | 1.85000 | 3133.6 | 1.38600 | 3132.5 |
| 340 | 2.82400 | 3155.1 | 1.88100 | 3153.9 | 1.41000 | 3152.9 |
| 350 | 2.87100 | 3175.3 | 1.91200 | 3174.3 | 1.43300 | 3173.3 |
| 360 | 2.91700 | 3195.7 | 1.94300 | 3194.8 | 1.45600 | 3193.8 |
| 370 | 2.96400 | 3216.2 | 1.97400 | 3215.3 | 1.47900 | 3214.4 |
| 380 | 3.01000 | 3236.7 | 2.00500 | 3235.9 | 1.50300 | 3235.0 |
| 390 | 3.05600 | 3257.3 | 2.03600 | 3256.5 | 1.52600 | 3255.7 |
| 400 | 3.10300 | 3278.0 | 2.06700 | 3277.2 | 1.54900 | 3276.4 |
| 410 | 3.14900 | 3298.7 | 2.09800 | 3297.9 | 1.57200 | 3297.2 |
| 420 | 3.19500 | 3319.5 | 2.12900 | 3318.7 | 1.59600 | 3318.0 |
| 430 | 3.24200 | 3340.3 | 2.16000 | 3339.6 | 1.61900 | 3338.9 |
| 440 | 3.28800 | 3361.2 | 2.19100 | 3360.5 | 1.64200 | 3359.8 |
| 450 | 3.33400 | 3382.2 | 2.22200 | 3381.5 | 1.66500 | 3380.8 |
|  | р = 0.25 MPa |  | р = 0.3 MPa |  | р = 0.4 MPa |  |
| 130 | 0.72410 | 2722.7 | - | - | - | - |
| 140 | 0.74430 | 2744.0 | 0.61700 | 2739.6 | - | - |
| 150 | 0.76440 | 2765.1 | 0.63400 | 2761.2 | 0.47080 | 2752.9 |
| 160 | 0.78420 | 2786.0 | 0.65080 | 2782.4 | 0.48390 | 2775.0 |
| 170 | 0.80340 | 2806.7 | 0.66740 | 2803.4 | 0.49670 | 2796.8 |
| 180 | 0.82330 | 2827.2 | 0.68380 | 2824.3 | 0.50940 | 2818.3 |
| 190 | 0.84270 | 2847.6 | 0.70020 | 2845.0 | 0.52190 | 2839.5 |
| 200 | 0.86200 | 2868.0 | 0.71640 | 2865.6 | 0.53430 | 2860.6 |
| 210 | 0.88120 | 2888.3 | 0.73250 | 2886.1 | 0.54660 | 2881.5 |
| 220 | 0.90040 | 2908.5 | 0.74860 | 2906.5 | 0.55880 | 2902.2 |
| 230 | 0.91940 | 2928.8 | 0.76460 | 2926.9 | 0.57100 | 2922.9 |
| 240 | 0.93840 | 2949.0 | 0.78050 | 2947.2 | 0.58310 | 2943.5 |
| 250 | 0.95740 | 2969.2 | 0.79640 | 2967.5 | 0.59520 | 2964.1 |
| 260 | 0.97630 | 2989.4 | 0.81230 | 2987.8 | 0.60710 | 2984.6 |
| 270 | 0.99520 | 3009.6 | 0.82810 | 3008.1 | 0.61910 | 3005.2 |
| 280 | 1.01400 | 3029.8 | 0.84380 | 3028.5 | 0.63110 | 3025.7 |
| 290 | 1.03300 | 3050.0 | 0.85960 | 3048.8 | 0.64300 | 3046.2 |
| 300 | 1.05200 | 3070.4 | 0.87530 | 3069.2 | 0.65480 | 3066.7 |
| 310 | 1.07000 | 3090.7 | 0.89100 | 3089.6 | 0.66670 | 3087.2 |
| 320 | 1.08900 | 3111.0 | 0.90670 | 3110.0 | 0.67850 | 3107.7 |
|  | р = 0.25 MPa |  | р = 0.3 MPa |  | р = 0.4MPa |  |
| 330 | 0.10800 | 3131.5 | 0.92230 | 3130.4 | 0.69030 | 3128.3 |
| 340 | 0.12700 | 3151.9 | 0.93800 | 3150.9 | 0.70210 | 3148.9 |
| 350 | 0.14500 | 3172.4 | 0.95360 | 3171.4 | 0.71390 | 3169.5 |
| 360 | 0.16400 | 3192.9 | 0.96920 | 3192.0 | 0.72570 | 3190.1 |
| 370 | 0.18300 | 3213.5 | 0.98480 | 3212.7 | 0.73740 | 3210.9 |
| 380 | 0.20100 | 3234.2 | 1.00000 | 3233.4 | 0.74920 | 3231.7 |
| 390 | 0.22000 | 3254.9 | 1.01600 | 3254.1 | 0.76090 | 3252.5 |
| 400 | 0.23800 | 3275.6 | 1.03100 | 3274.9 | 0.77260 | 3273.3 |
| 410 | 0.25700 | 3296.4 | 1.04700 | 3295.7 | 0.78430 | 3294.2 |
| 420 | 0.27600 | 3317.3 | 1.06200 | 3316.6 | 0.79600 | 3315.2 |
| 430 | 0.29400 | 3338.2 | 1.07800 | 3337.5 | 0.80770 | 3336.2 |
| 440 | 0.31300 | 3359.2 | 1.09400 | 3358.5 | 0.81930 | 3357.2 |
| 450 | 0.33200 | 3380.2 | 1.10900 | 3379.6 | 0.83100 | 3378.3 |
|  | р = 0.5MPa |  | р = 0.6 MPa |  | р = 0.7 MPa |  |
| 160 | 0.38360 | 2767.4 | 0.31660 | 2759.2 | - | - |
| 170 | 0.39420 | 2789.9 | 0.32580 | 2782.7 | 0.27680 | 2775.2 |
| 180 | 0.40460 | 2812.1 | 0.33470 | 2805.6 | 0.28470 | 2798.9 |
| 190 | 0.41480 | 2833.9 | 0.34340 | 2828.1 | 0.29240 | 2822.1 |
| 200 | 0.42490 | 2855.4 | 0.35210 | 2850.2 | 0.29990 | 2844.8 |
| 210 | 0.43490 | 2876.8 | 0.36060 | 2872.0 | 0.30740 | 2867.1 |
| 220 | 0.44490 | 2897.9 | 0.36900 | 2893.6 | 0.31470 | 2889.1 |
| 230 | 0.45480 | 2918.9 | 0.37740 | 2914.9 | 0.32200 | 2910.8 |
| 240 | 0.46460 | 2939.9 | 0.38570 | 2936.1 | 0.32920 | 2932.3 |
| 250 | 0.47440 | 2960.7 | 0.39390 | 2957.2 | 0.33630 | 2953.7 |
| 260 | 0.48410 | 2981.4 | 0.40210 | 2978.2 | 0.34340 | 2974.9 |
| 270 | 0.49380 | 3002.1 | 0.41020 | 2999.1 | 0.35050 | 2996.1 |
| 280 | 0.50340 | 3022.8 | 0.41830 | 3020.0 | 0.35750 | 3017.2 |
| 290 | 0.51300 | 3043.5 | 0.42640 | 3040.9 | 0.36440 | 3038.2 |
| 300 | 0.52260 | 3064.2 | 0.43440 | 3061.7 | 0.37140 | 3059.1 |
| 310 | 0.53210 | 3084.8 | 0.44240 | 3082.4 | 0.37830 | 3080.0 |
| 320 | 0.54160 | 3105.5 | 0.45040 | 3103.2 | 0.38520 | 3100.9 |
| 330 | 0.55110 | 3126.1 | 0.45840 | 3124.0 | .0.3921 | 3121.8 |
| 340 | 0.56060 | 3146.8 | 0.46630 | 3144.8 | 0.39890 | 3142.7 |
| 350 | 0.57010 | 3167.5 | 0.47420 | 3165.6 | 0.40570 | 3163.6 |
| 360 | 0.57960 | 3188.3 | 0.48210 | 3186.4 | 0.41260 | 3184.6 |
| 370 | 0.58900 | 3209.1 | 0.49000 | 3207.4 | 0.41940 | 3205.6 |
| 380 | 0.59840 | 3230.0 | 0.49790 | 3228.4 | 0.42620 | 3226.6 |
| 390 | 0.60780 | 3250.9 | 0.50580 | 3249.3 | 0.43290 | 3247.7 |
| 400 | 0.61720 | 3271.8 | 0.51370 | 3270.3 | 0.43970 | 3268.7 |
| 410 | 0.62660 | 3292.7 | 0.52150 | 3291.3 | 0.44650 | 3289.8 |
| 420 | 0.63600 | 3313.7 | 0.52940 | 3312.4 | 0.45320 | 3310.9 |
| 430 | 0.64540 | 3334.8 | 0.53720 | 3333.5 | 0.46000 | 3332.1 |
| 440 | 0.65480 | 3355.9 | 0.54510 | 3354.6 | 0.46670 | 3353.3 |
| 450 | 0.66410 | 3377.0 | 0.55290 | 3375.8 | 0.47340 | 3374.5 |
| 460 | 0.67350 | 3398.2 | 0.56070 | 3397.1 | 0.48010 | 3395.8 |
| 470 | 0.68280 | 3419.5 | 0.56850 | 3418.4 | 0.48690 | 3417.2 |
| 480 | 0.69220 | 3440.8 | 0.57630 | 3439.7 | 0.49360 | 3438.6 |
| 490 | 0.70150 | 3462.2 | 0.58410 | 3461.1 | 0.50030 | 3460.0 |
| 500 | 0.71090 | 3483.6 | 0.59190 | 3482.6 | 0.50700 | 3481.5 |
| 510 | 0.72020 | 3505. 1 | 0.59970 | 3504.1 | 0.51370 | 3503.1 |
| 520 | 0.72950 | 3526.7 | 0.60750 | 3525.7 | 0.52040 | 3524.7 |
| 530 | 0.73880 | 3548.3 | 0.61530 | 3547.4 | 0.52700 | 3546.4 |
| 540 | 0.74820 | 3570.0 | 0.62310 | 3569.1 | 0.53370 | 3568.1 |
| 550 | 0.75750 | 3591.7 | 0.63090 | 3590.8 | 0.54040 | 3589.9 |
| 560 | - | - | - | - | 0.54710 | 3611.8 |
| 570 | - | - | - | - | 0.55370 | 3633.7 |
|  | р = 0.5 MPa |  | р = 0.6 MPa |  | р = 0.7 MPa |  |
| 580 | - | - | - | - | 0.56040 | 3655.7 |
| 590 | - | - | - | - | 0.56710 | 3677.7 |
| 600 | - | - | - | - | 0.57370 | 3699.8 |
| 610 | - | - | - | - | 0.58040 | 3722.0 |
| 620 | - | - | - | - | 0.58700 | 3744.2 |
| 630 | - | - | - | - | 0.59370 | 3766.4 |
| 640 | - | - | - | - | 0.60040 | 3788.8 |
| 650 | - | - | - | - | 0.60700 | 3811.2 |
|  | р = 0.8 MPa |  | р = 0.9 MPa |  | р = 1.0 MPa |  |
| 180 | 0.24710 | 2792.0 | 0.21780 | 2784.8 | 0.19440 | 2777.3 |
| 190 | 0.25400 | 2815.9 | 0.22420 | 2809.5 | 0.20020 | 2802.9 |
| 200 | 0.26080 | 2839.2 | 0.23040 | 2833.5 | 0.20590 | 2827.5 |
| 210 | 0.26750 | 2862.0 | 0.23640 | 2856.9 | 0.21150 | 2851.5 |
| 220 | 0.27400 | 2884.5 | 0.24230 | 2879.8 | 0.21690 | 2874.9 |
| 230 | 0.28050 | 2906.6 | 0.24810 | 2902.3 | 0.22230 | 2897.9 |
| 240 | 0.28690 | 2928.4 | 0.25390 | 2924.5 | 0.22750 | 2920.5 |
| 250 | 0.29320 | 2950.1 | 0.25960 | 2946.5 | 0.23270 | 2942.8 |
| 260 | 0.29950 | 2971.6 | 0.26520 | 2968.2 | 0.23780 | 2964.8 |
| 270 | 0.30570 | 2993.0 | 0.27080 | 2989.8 | 0.24290 | 2986.7 |
| 280 | 0.31190 | 3014.2 | 0.27640 | 3011.3 | 0.24800 | 3008.3 |
| 290 | 0.31800 | 3035.4 | 0.28190 | 3032.7 | 0.25300 | 3029.9 |
| 300 | 0.32410 | 3056.5 | 0.28740 | 3054.0 | 0.25800 | 3051.3 |
| 310 | 0.33020 | 3077.6 | 0.29280 | 3075.2 | 0.26290 | 3072.7 |
| 320 | 0.33630 | 3098.7 | 0.29830 | 3096.3 | 0.26780 | 3094.0 |
| 330 | 0.34230 | 3119.7 | 0.30370 | 3117.5 | 0.27270 | 3115.3 |
| 340 | 0.34840 | 3140.7 | 0.30910 | 3138.6 | 0.27760 | 3136.5 |
| 350 | 0.35440 | 3161.7 | 0.31440 | 3159.7 | 0.28250 | 3157.7 |
| 360 | 0.36040 | 3182.7 | 0.31980 | 3180.8 | 0.28730 | 3178.9 |
| 370 | 0.36640 | 3203.3 | 0.32510 | 3202.0 | 0.29210 | 3200.2 |
| 380 | 0.37230 | 3225.0 | 0.33040 | 3223.2 | 0.29700 | 3221.5 |
| 390 | 0.37830 | 3246.1 | 0.33580 | 3244.4 | 0.30180 | 3242.8 |
| 400 | 0.38420 | 3267.2 | 0.34110 | 3265.6 | 0.30660 | 3264.0 |
| 410 | 0.39020 | 3288.3 | 0.34640 | 3286.8 | 0.31130 | 3285.3 |
| 420 | 0.39610 | 3309.5 | 0.35170 | 3308.1 | 0.31610 | 3306.6 |
| 430 | 0.40200 | 3330.7 | 0.35690 | 3329.3 | 0.32090 | 3327.9 |
| 440 | 0.40790 | 3352.0 | 0.36220 | 3350.6 | 0.32560 | 3349.3 |
| 460 | 0.41970 | 3394.6 | 0.37270 | 3393.4 | 0.33510 | 3392.1 |
| 470 | 0.42560 | 3416.0 | 0.37800 | 3414.8 | 0.33990 | 3413.6 |
| 480 | 0.43150 | 3437.4 | 0.38320 | 3436.3 | 0.34460 | 3435.1 |
| 490 | 0.43740 | 3458.9 | 0.38850 | 3457.8 | 0.34930 | 3456.7 |
| 500 | 0.44320 | 3480.5 | 0.39370 | 3479.4 | 0.35400 | 3478.3 |
| 510 | 0.44910 | 3502.1 | 0.39890 | 3501.0 | 0.35880 | 3500.0 |
| 520 | 0.45500 | 3523.7 | 0.40410 | 3522.7 | 0.36350 | 3521.7 |
| 530 | 0.46080 | 3545.4 | 0.40940 | 3544.4 | 0.36820 | 3543.5 |
| 540 | 0.46670 | 3567.2 | 0.41460 | 3566.2 | 0.37290 | 3565.3 |
| 550 | 0.47250 | 3589.0 | 0.41980 | 3588.1 | 0.37760 | 3587.2 |
| 560 | 0.47840 | 3610.9 | 0.42500 | 3610.0 | 0.38230 | 3609.1 |
| 570 | 0.48420 | 3632.8 | 0.43020 | 3632.0 | 0.38700 | 3631.1 |
| 580 | 0.49010 | 3654.8 | 0.43540 | 3654.0 | 0.39160 | 3653.2 |
| 590 | 0.49590 | 3676.9 | 0.44060 | 3676.1 | 0.39630 | 3675.3 |
| 600 | 0.50180 | 3699.0 | 0.44580 | 3698.2 | 0.40100 | 3697.4 |
| 610 | 0.50760 | 3721.2 | 0.45100 | 3720.4 | 0.40570 | 3719.6 |
| 620 | 0.51340 | 3743.4 | 0.45620 | 3742.7 | 0.41040 | 3741.9 |
| 630 | 0.51930 | 3765.7 | 0.46140 | 3765.0 | 0.41510 | 3764.2 |
| 640 | 0.52510 | 3788.1 | 0.46660 | 3787.4 | 0.41970 | 3786.6 |
| 650 | 0.53090 | 3810.5 | 0.47180 | 3809.8 | 0.42440 | 3809.1 |
|  | р = 1.1 MPa |  | р = 1.2 MPa |  | р = 1.3 MPa |  |
| 190 | 0.18060 | 2796.0 | 0.16420 | 2788.9 | - | - |
| 200 | 0.18590 | 2821.5 | 0.16920 | 2815.2 | 0.15510 | 2808.8 |
| 210 | 0.19110 | 2846.1 | 0.17410 | 2840.5 | 0.15970 | 2834.8 |
| 220 | 0.19620 | 2870.0 | 0.17880 | 2865.0 | 0.16410 | 2859.9 |
| 230 | 0.20110 | 2893.4 | 0.18340 | 2888.9 | 0.16840 | 2884.2 |
| 240 | 0.20590 | 2916.4 | 0.18790 | 2912.2 | 0.17270 | 2908.0 |
| 250 | 0.21070 | 2939.0 | 0.19240 | 2935.2 | 0.17680 | 2931.3 |
| 260 | 0.21540 | 2961.2 | 0.19680 | 2957.8 | 0.18090 | 2954.2 |
| 270 | 0.22010 | 2983.4 | 0.20110 | 2980.2 | 0.18500 | 2976.8 |
| 280 | 0.22470 | 3005.3 | 0.20540 | 3002.3 | 0.18900 | 2999.2 |
| 290 | 0.22930 | 3027.1 | 0.20960 | 3024.2 | 0.19290 | 3021.4 |
| 300 | 0.23390 | 3048.7 | 0.21380 | 3046.0 | 0.19680 | 3043.4 |
| 310 | 0.23840 | 3070.2 | 0.21800 | 3067.7 | 0.20070 | 3065.2 |
| 320 | 0.24290 | 3091.6 | 0.22220 | 3089.3 | 0.20460 | 3086.9 |
| 330 | 0.24740 | 3113.0 | 0.22630 | 3110.8 | 0.20840 | 3108.5 |
| 340 | 0.25190 | 3134.4 | 0.23040 | 3132.2 | 0.21230 | 3130.1 |
| 350 | 0.25530 | 3155.7 | 0.23450 | 3153.7 | 0.21610 | 3151.7 |
| 360 | 0.26070 | 3177.0 | 0.23860 | 31.75.1 | 0.21990 | 3173.2 |
| 370 | 0.26520 | 3198.4 | 0.24260 | 3196.6 | 0.22360 | 3194.8 |
| 380 | 0.26960 | 3219.8 | 0.24670 | 3218.1 | 0.22740 | 3216.3 |
| 390 | 0.27390 | 3241.1 | 0.25070 | 3239.5 | 0.23110 | 3237.6 |
| 400 | 0.27830 | 3262.5 | 0.25480 | 3260.9 | 0.23480 | 3259.3 |
| 410 | 0.28270 | 3283.8 | 0.25880 | 3282.3 | 0.23860 | 3280.8 |
| 420 | 0.28700 | 3305.2 | 0.26280 | 3303.7 | 0.24230 | 3302.3 |
| 430 | 0.29140 | 3326.5 | 0.26680 | 3325.1 | 0.24600 | 3323.7 |
| 440 | 0.29570 | 3347.9 | 0.27080 | 3346.6 | 0.24970 | 3345.3 |
| 450 | 0.30000 | 3369.4 | 0.27480 | 3368.1 | 0.25340 | 3366.8 |
| 460 | 0.30440 | 3390.9 | 0.27870 | 3389.6 | 0.25700 | 3388.4 |
| 470 | 0.30870 | 3412.4 | 0.28270 | 3411.2 | 0.26070 | 3410.0 |
| 480 | 0.31300 | 3434.0 | 0.28670 | 3432.8 | 0.26440 | 3431.6 |
| 490 | 0.31730 | 3455.6 | 0.29060 | 3454.4 | 0.26800 | 3453.3 |
| 500 | 0.32160 | 3477.2 | 0.29460 | 3476.1 | 0.27170 | 3475.1 |
| 510 | 0.32590 | 3498.9 | 0.29850 | 3497.9 | 0.27530 | 3496.8 |
| 520 | 0.33020 | 3520.7 | 0.30250 | 3519.7 | 0.27900 | 3518.7 |
| 530 | 0.33450 | 3542.7 | 0.30640 | 3541.5 | 0.28260 | 3540.5 |
| 540 | 0.33880 | 3564.3 | 0.31030 | 3563.4 | 0.28630 | 3562.4 |
| 550 | 0.34300 | 3586.2 | 0.31420 | 3585.3 | 0.28990 | 3584.4 |
| 560 | 0.34730 | 3608.2 | 0.31820 | 3607.3 | 0.29350 | 3606.4 |
| 570 | 0.35160 | 3630.2 | 0.32210 | 3629.4 | 0.29720 | 3628.5 |
| 580 | 0.35590 | 3652.3 | 0.32600 | 3651.5 | 0.30080 | 3650.6 |
| 590 | 0.36010 | 3674.4 | 0.32990 | 3673.6 | 0.30440 | 3672.8 |
| 600 | 0.36440 | 3696.6 | 0.33390 | 3695.8 | 0.30800 | 3695.0 |
| 610 | 0.36860 | 3718.9 | 0.33780 | 3718.1 | 0.31160 | 3717.3 |
| 620 | 0.37290 | 3741.2 | 0.34170 | 3740.4 | 0.31530 | 3739.7 |
| 630 | 0.37720 | 3763.5 | 0.34560 | 3762.8 | 0.31890 | 3762.1 |
| 640 | 0.38140 | 3785.9 | 0.34950 | 3785.2 | 0.32250 | 3784.5 |
| 650 | 0.38570 | 3808.4 | 0.35340 | 3807.7 | 0.32610 | 3807.0 |
|  | р = 1.4 MPa |  | р = 1.5 MPa |  | р = 1.6 MPa |  |
| 200 | 0.14290 | 2802.1 | 0.13240 | 2795.3 | - | - |
| 210 | 0.14730 | 2828.9 | 0.13660 | 2822.9 | 0.12710 | 2816.7 |
| 220 | 0.15150 | 2854.5 | 0.14060 | 2849.2 | 0.13100 | 2843.7 |
| 230 | 0.15560 | 2879.5 | 0.14450 | 2874.7 | 0.13470 | 2869.8 |
| 240 | 0.15960 | 2903.7 | 0.14830 | 2899.3 | 0.13830 | 2894.9 |
| 250 | 0.16350 | 2927.4 | 0.15200 | 2923.4 | 0.14190 | 2919.4 |
| 260 | 0.16740 | 2950.6 | 0.15560 | 2947.0 | 0.14530 | 2943.3 |
| 270 | 0.17120 | 2973.5 | 0.15920 | 2970.2 | 0.14870 | 2966.7 |
| 280 | 0.17490 | 2996.0 | 0.16270 | 2993.0 | 0.15210 | 2989.8 |
| 290 | 0.17860 | 3018.0 | 0.16620 | 3015.6 | 0.15540 | 3012.7 |
| 300 | 0.18230 | 3040.7 | 0.16970 | 3037.9 | 0.15860 | 3035.2 |
| 310 | 0.18590 | 3062.7 | 0.17310 | 3060.0 | 0.16190 | 3057.5 |
| 320 | 0.18950 | 3084.5 | 0.17650 | 3082.1 | 0.16510 | 3079.7 |
| 330 | 0.19310 | 3106.3 | 0.17990 | 3104.0 | 0.16830 | 3101.7 |
| 340 | 0.19670 | 3128.0 | 0.18320 | 3125.8 | 0.17140 | 3123.6 |
| 350 | 0.20020 | 3149.6 | 0.18660 | 3147.6 | 0.17460 | 3145.5 |
| 360 | 0.20380 | 3171.2 | 0.18990 | 3169.3 | 0.17770 | 3167.4 |
| 370 | 0.20730 | 3192.9 | 0.19320 | 3191.1 | 0.18080 | 3189.3 |
| 380 | 0.21080 | 3214.6 | 0.19640 | 3212.8 | 0.18390 | 3211.1 |
| 390 | 0.21430 | 3236.2 | 0.19970 | 3234.5 | 0.18700 | 3232.8 |
| 400 | 0.21780 | 3257.7 | 0.20300 | 3256.1 | 0.19000 | 3254.5 |
| 410 | 0.22120 | 3279.3 | 0.20620 | 3277.7 | 0.19310 | 3276.2 |
| 420 | 0.22470 | 3300.8 | 0.20950 | 3299.3 | 0.19610 | 3297.9 |
| 430 | 0.22810 | 3322.3 | 0.21270 | 3320.9 | 0.19920 | 3319.5 |
| 440 | 0.23160 | 3343.9 | 0.21590 | 3342.6 | 0.20220 | 3341.2 |
| 450 | 0.23500 | 3365.5 | 0.21910 | 3364.2 | 0.20520 | 3362.9 |
| 460 | 0.23840 | 3387.1 | 0.22230 | 3385.9 | 0.20820 | 3384.6 |
| 470 | 0.24190 | 3408.8 | 0.22550 | 3407.6 | 0.21120 | 3406.4 |
| 480 | 0.24530 | 3430.5 | 0.22870 | 3429.3 | 0.21420 | 3428.1 |
| 490 | 0.24870 | 3452.2 | 0.23190 | 3451.1 | 0.21720 | 3449.9 |
| 500 | 0.25210 | 3474.0 | 0.23510 | 3472.9 | 0.22020 | 3471.8 |
| 510 | 0.25550 | 3495.8 | 0.23830 | 3494.7 | 0.22320 | 3493.7 |
| 520 | 0.25890 | 3517.6 | 0.24140 | 3516.6 | 0.22620 | 3515.6 |
| 530 | 0.26230 | 3539.5 | 0.24460 | 3538.6 | 0.22920 | 3537.6 |
| 540 | 0.26570 | 3561.5 | 0.24780 | 3560.5 | 0.23220 | 3559.6 |
| 550 | 0.26900 | 3583.5 | 0.25090 | 3582.5 | 0.23510 | 3581.6 |
| 560 | 0.27240 | 3605.5 | 0.25410 | 3604.6 | 0.23810 | 3603.7 |
| 570 | 0.27580 | 3627.6 | 0.25720 | 3626.8 | 0.24100 | 3625.9 |
| 580 | 0.27920 | 3649.8 | 0.26040 | 3649.0 | 0.24400 | 3648.1 |
| 590 | 0.28250 | 3672.0 | 0.26360 | 3671.2 | 0.24700 | 3670.4 |
| 600 | 0.28590 | 3694.3 | 0.26670 | 3693.5 | 0.24990 | 3692.7 |
| 610 | 0.28920 | 3716.6 | 0.26980 | 3715.8 | 0.25290 | 3715.0 |
| 620 | 0.29260 | 3738.9 | 0.27300 | 3738.2 | 0.25580 | 3737.4 |
| 630 | 0.29600 | 3761.3 | 0.27610 | 3760.6 | 0.25880 | 3759.8 |
| 640 | 0.29930 | 3783.8 | 0.27930 | 3783.1 | 0.26170 | 3782.3 |
| 650 | 0.30270 | 3806.3 | 0.28240 | 3805.6 | 0.26460 | 3804.9 |
|  | р = 1.7 MPa |  | р = 1.8 MPa |  | р = 1.9 MPa |  |
| 210 | 0.11880 | 2810.3 | 0.11140 | 2803.7 | 0.10470 | 2797.0 |
| 220 | 0.12250 | 2838.1 | 0.11500 | 2832.3 | 0.10820 | 2826.4 |
| 230 | 0.12610 | 2864.7 | 0.11840 | 2859.6 | 0.11150 | 2854.3 |
| 240 | 0.12960 | 2890.4 | 0.12180 | 2885.8 | 0.11480 | 2881.1 |
| 250 | 0.13290 | 2915.2 | 0.12500 | 2911.1 | 0.11790 | 2906.8 |
| 260 | 0.13620 | 2939.5 | 0.12810 | 2935.7 | 0.12090 | 2931.8 |
| 270 | 0.13950 | 2963.3 | 0.13120 | 2959.8 | 0.12390 | 2956.3 |
| 280 | 0.14270 | 2986.7 | 0.13430 | 2983.4 | 0.12680 | 2980.2 |
| 290 | 0.14580 | 3009.7 | 0.13730 | 3006.7 | 0.12960 | 3003.7 |
| 300 | 0.14890 | 3032.4 | 0.14020 | 3029.6 | 0.13250 | 3026.8 |
| 310 | 0.15200 | 3054.9 | 0.14310 | 3052.3 | 0.13530 | 3049.7 |
| 320 | 0.15500 | 3077.2 | 0.14600 | 3074.8 | 0.13800 | 3072.3 |
| 330 | 0.15800 | 3099.4 | 0.14890 | 3097.1 | 0.14070 | 3094.8 |
| 340 | 0.16100 | 3121.5 | 0.15170 | 3119.3 | 0.14340 | 3117.1 |
| 350 | 0.16400 | 3143.5 | 0.15460 | 3141.4 | 0.14610 | 3139.3 |
| 360 | 0.16690 | 3165.4 | 0.15740 | 3163.5 | 0.14880 | 3161.5 |
| 370 | 0.16990 | 3187.4 | 0.16020 | 3185.6 | 0.15150 | 3183.7 |
| 380 | 0.17280 | 3209.3 | 0.16290 | 3207.6 | 0.15410 | 3205.8 |
| 390 | 0.17570 | 3231.2 | 0.16570 | 3229.5 | 0.15670 | 3227.8 |
| 400 | 0.17860 | 3253.0 | 0.16840 | 3251.3 | 0.15930 | 3249.7 |
| 410 | 0.18150 | 3274.7 | 0.17120 | 3273.1 | 0.16190 | 3271.6 |
| 420 | 0.18440 | 3296.4 | 0.17390 | 3294.9 | 0.16450 | 3293.4 |
| 430 | 0.18720 | 3318.1 | 0.17660 | 3316.7 | 0.16710 | 3315.3 |
| 440 | 0.19010 | 3339.8 | 0.17930 | 3338.5 | 0.16970 | 3337.1 |
| 450 | 0.19290 | 3361.6 | 0.18200 | 3360.3 | 0.17230 | 3359.0 |
| 460 | 0.19580 | 3383.4 | 0.18470 | 3382.1 | 0.17480 | 3380.8 |
| 470 | 0.19860 | 3405.2 | 0.18740 | 3403.9 | 0.17740 | 3402.7 |
| 480 | 0.20150 | 3427.0 | 0.19010 | 3425.8 | 0.17990 | 3424.6 |
| 490 | 0.20430 | 3448.8 | 0.19280 | 3447.7 | 0.18250 | 3446.6 |
| 500 | 0.20710 | 3470.7 | 0.19540 | 3469.6 | 0.18500 | 3468.5 |
| 510 | 0.20990 | 3492.6 | 0.19810 | 3491.6 | 0.18750 | 3490.5 |
| 520 | 0.21270 | 3514.6 | 0.20080 | 3513.6 | 0.19010 | 3512.5 |
| 530 | 0.21550 | 3536.6 | 0.20340 | 3535.6 | 0.19260 | 3534.6 |
| 540 | 0.21830 | 3558.6 | 0.20610 | 3557.7 | 0.19510 | 3556.7 |
| 550 | 0.22110 | 3580.7 | 0.20870 | 3579.8 | 0.19760 | 3578.9 |
| 560 | 0.22390 | 3602.8 | 0.21140 | 3602.0 | 0.20010 | 3601.1 |
| 570 | 0.22670 | 3625.0 | 0.21400 | 3624.2 | 0.20260 | 3623.3 |
| 580 | 0.22950 | 3647.3 | 0.21660 | 3646.4 | 0.20510 | 3645.6 |
| 590 | 0.23230 | 3669.3 | 0.21930 | 3668.7 | 0.20760 | 3667.9 |
| 600 | 0.23510 | 3691.9 | 0.22190 | 3691.1 | 0.21010 | 3690.3 |
| 610 | 0.23790 | 3714.2 | 0.22460 | 3713.5 | 0.21260 | 3712.7 |
| 620 | 0.24060 | 3736.6 | 0.22720 | 3735.9 | 0.21510 | 3735.1 |
| 630 | 0.24340 | 3759.1 | 0.22980 | 3758.4 | 0.21760 | 3757.6 |
| 640 | 0.24620 | 3781.6 | 0.23240 | 3780.9 | 0.22010 | 3780.2 |
| 650 | 0.24900 | 3804.2 | 0.23510 | 3803.5 | 0.22260 | 3802.8 |
|  | р = 2.0 MPa |  | р = 2.1 MPa |  | р = 2.2 MPa |  |
| 220 | 0.10210 | 2820.4 | 0.09657 | 2814.2 | 0.09152 | 2807.8 |
| 230 | 0.10530 | 2849.0 | 0.09972 | 2843.5 | 0.09460 | 2837.9 |
| 240 | 0.10840 | 2876.3 | 0.10274 | 2871.4 | 0.09754 | 2866.4 |
| 250 | 0.11150 | 2902.5 | 0.10570 | 2898.2 | 0.10037 | 2893.7 |
| 260 | 0.11440 | 2927.9 | 0.10850 | 2924.0 | 0.10310 | 2919.9 |
| 270 | 0.11720 | 2952.7 | 0.11120 | 2949.0 | 0.10580 | 2945.4 |
| 280 | 0. 1 200 | 2976.9 | 0.11390 | 2973.5 | 0.10840 | 2970.2 |
| 290 | 0.12280 | 3000.6 | 0.11660 | 2997.5 | 0.11090 | 2994.4 |
| 300 | 0.12550 | 3024.0 | 0.11920 | 3021.1 | 0.11340 | 3018.2 |
| 310 | 0.12820 | 3047.0 | 0.12170 | 3044.4 | 0.11590 | 3041.7 |
| 320 | 0.13080 | 3069.8 | 0.12430 | 3067.3 | 0.11830 | 3064.8 |
| 330 | 0.13340 | 3092.4 | 0.12680 | 3090.0 | 0.12070 | 3087.7 |
| 340 | 0.13600 | 3114.9 | 0.12930 | 3112.6 | 0.12310 | 3110.4 |
| 350 | 0.13860 | 3137.2 | 0.13170 | 3135.1 | 0.12550 | 3133.0 |
| 360 | 0.14110 | 3159.5 | 0.13420 | 3157.6 | 0.12780 | 3155.6 |
| 370 | 0.14360 | 3181.8 | 0.13660 | 3180.0 | 0.13010 | 3178.1 |
| 380 | 0.14620 | 3204.0 | 0.13900 | 3202.2 | 0.13250 | 3200.4 |
| 390 | 0.14870 | 3226.1 | 0.14140 | 3224.4 | 0.13480 | 3222.7 |
| 400 | 0.15120 | 3248.1 | 0.14380 | 3246.5 | 0.13700 | 3244.8 |
| 410 | 0.15360 | 3270.0 | 0.14610 | 3268.5 | 0.13930 | 3266.9 |
| 420 | 0.15610 | 3291.9 | 0.14850 | 3290.5 | 0.14160 | 3289.0 |
| 430 | 0.15860 | 3313.8 | 0.15080 | 3312.4 | 0.14380 | 3311.0 |
| 440 | 0.16100 | 3335.8 | 0.15320 | 3334.4 | 0.14610 | 3333.0 |
| 450 | 0.16350 | 3357.7 | 0.15550 | 3356.3 | 0.14830 | 3355.0 |
| 460 | 0.16590 | 3379.6 | 0.15790 | 3378.3 | 0.15050 | 3377.0 |
| 470 | 0.16840 | 3401.5 | 0.16020 | 3400.3 | 0.15280 | 3399.1 |
| 480 | 0.17080 | 3423.5 | 0.16250 | 3422.3 | 0.15500 | 3421.1 |
| 490 | 0.17320 | 3445.4 | 0.16480 | 3444.3 | 0.15720 | 3443.2 |
| 500 | 0.17560 | 3467.4 | 0.16710 | 3466.3 | 0. 1 594 | 3465.2 |
| 510 | 0.17800 | 3489.5 | 0.16940 | 3488.4 | 0.16160 | 3487.3 |
| 520 | 0.18040 | 3511.5 | 0.17170 | 3510.5 | 0.16380 | 3509.4 |
| 530 | 0.18280 | 3533.6 | 0.17400 | 3532.6 | 0.16600 | 3531.6 |
| 540 | 0.18520 | 3555.8 | 0.17630 | 3554.8 | 0.16820 | 3553.8 |
| 550 | 0.18760 | 3578.0 | 0.17860 | 3577.0 | 0.17030 | 3576.1 |
| 560 | 0.19000 | 3600.2 | 0.18080 | 3599.3 | 0.17250 | 3598.4 |
| 570 | 0.19240 | 3622.5 | 0.18310 | 3621.6 | 0.17470 | 3620.7 |
| 580 | 0.19480 | 3644.8 | 0.18540 | 3643.9 | 0.17690 | 3643.1 |
| 590 | 0.19720 | 3667.1 | 0.18760 | 3666.2 | 0.17900 | 3665.5 |
| 600 | 0.19950 | 3689.5 | 0.18990 | 3688.6 | 0.18120 | 3687.9 |
| 610 | 0.20190 | 3711.9 | 0.19220 | 3711.1 | 0.18340 | 3710.4 |
| 620 | 0.20430 | 3734.4 | 0.19450 | 3733.6 | 0.18550 | 3732.9 |
| 630 | 0.20660 | 3756.9 | 0.19670 | 3756.2 | 0.18770 | 3755.4 |
| 640 | 2090.00000 | 3779.5 | 0.19900 | 3778.8 | 0.18990 | 3778.0 |
| 650 | 0.21140 | 3802.1 | 0.20120 | 3801.4 | 0.19200 | 3800.7 |
|  | р = 2.3 MPa |  | р = 2.4 MPa |  | р = 2.5 MPa |  |
| 220 | 0.08690 | 2801.2 | - | - | - | - |
| 230 | 0.08992 | 2832.2 | 0.08561 | 2826.4 | 0.08164 | 2820.4 |
| 240 | 0.09279 | 2861.4 | 0.08842 | 2856.2 | 0.08439 | 2851.0 |
| 250 | 0.09554 | 2889.2 | 0.09110 | 2884.6 | 0.08701 | 2879.9 |
| 260 | 0.09819 | 2915.8 | 0.09368 | 2911.7 | 0.08953 | 2907.5 |
| 270 | 0.10077 | 2941.6 | 0.09619 | 2937.9 | 0.09197 | 2934.1 |
| 280 | 0.10328 | 2966.7 | 0.09863 | 2963.3 | 0.09434 | 2959.8 |
| 290 | 0.10570 | 2991.2 | 0.10101 | 2988.1 | 0.09665 | 2984.9 |
| 300 | 0.10810 | 3015.3 | 0.10330 | 3012.4 | 0.09822 | 3009.4 |
| 310 | 0.11050 | 3039.0 | 0.10560 | 3036.2 | 0.10114 | 3033.4 |
| 320 | 0.11290 | 3062.3 | 0.10790 | 3059.7 | 0.10334 | 3057.1 |
| 330 | 0.11520 | 3085.3 | 0.11020 | 3082.9 | 0.10550 | 3080.5 |
| 340 | 0.11750 | 3108.2 | 0.11240 | 3105.9 | 0.10760 | 3103.6 |
| 350 | 0.11980 | 3130.9 | 0.11460 | 3128.8 | 0.10980 | 3126.6 |
| 360 | 0.12200 | 3153.6 | 0.11670 | 3151.6 | 0.11190 | 3149.6 |
| 370 | 0.12430 | 3176.2 | 0.11890 | 3174.3 | 0.11390 | 3172.4 |
| 380 | 0.12650 | 3198.6 | 0.12100 | 3196.8 | 0.11600 | 3195.0 |
| 390 | 0.12870 | 3221.0 | 0.12310 | 3219.2 | О.П80 | 3217.5 |
| 400 | 0.13090 | 3243.2 | 0.12530 | 3241.5 | 0.12010 | 3239.9 |
| 410 | 0.13310 | 3265.4 | 0.12740 | 3263.8 | 0.12210 | 3262.2 |
| 420 | 0.13520 | 3287.5 | 0.12940 | 3286.0 | 0.12410 | 3284.5 |
| 430 | 0.13740 | 3309.6 | 0.13150 | 3308.1 | 0.12610 | 3306.7 |
| 440 | 0.13960 | 3331.6 | 0.13360 | 3330.2 | 0.12810 | 3328.9 |
| 450 | 0.14170 | 3353.7 | 0.13570 | 3352.4 | 0.13010 | 3351.0 |
| 460 | 0.14380 | 3375.8 | 0.13770 | 3374.5 | 0.13210 | 3373.2 |
| 470 | 0.14600 | 3397.8 | 0.13980 | 3396.6 | 0.13400 | 3395.4 |
| 480 | 0.14810 | 3419.9 | 0.14180 | 3418.7 | 0.13600 | 3417.5 |
| 490 | 0.15020 | 3442.0 | 0.14380 | 3440.9 | 0.13800 | 3439.7 |
| 500 | 0.15230 | 3464.1 | 0.14590 | 3463.0 | 0.13990 | 3461.9 |
| 510 | 0.15440 | 3486.3 | 0.14790 | 3485.2 | 0.14190 | 3484. 1 |
| 520 | 0.15660 | 3508.4 | 0.14990 | 3507.4 | 0.14380 | 3506.4 |
| 530 | 0.15870 | 3530.6 | 0.15190 | 3529.6 | 0.14580 | 3528.7 |
| 540 | 0.16080 | 3552.9 | 0.15400 | 3551.9 | 0.14770 | 3551.0 |
| 550 | 0.16280 | 3575.2 | 0.15600 | 3574.2 | 0.14960 | 3573.3 |
| 560 | 0.16490 | 3597.5 | 0.15800 | 3596.6 | 0.15160 | 3595.7 |
| 570 | 0.16700 | 3619.8 | 0.16000 | 3619.0 | 0.15350 | 3618.1 |
| 580 | 0.16910 | 3642.2 | 0.16200 | 3641.4 | 0.15540 | 3640.5 |
| 590 | 0.17120 | 3664.6 | 0.16400 | 3663.8 | 0.15730 | 3663.0 |
| 600 | 0.17320 | 3687.1 | 0.16600 | 3686.3 | 0.15920 | 3685.5 |
| 610 | 0.17530 | 3709.6 | 0.16790 | 3708.8 | 0.16120 | 3708.0 |
| 620 | 0.17740 | 3732.0 | 0.16990 | 3731.4 | 0.16310 | 3730.6 |
| 630 | 0.17950 | 3754.7 | 0.17190 | 3754.0 | 0.16500 | 3753.2 |
| 640 | 0.18150 | 3777.3 | 0.17390 | 3776.6 | 0.16690 | 3775.9 |
| 650 | 0.18360 | 3800.0 | 0.17590 | 3799.3 | 0.16880 | 3798.6 |
|  | р = 2.6 MPa |  | р = 2.7 MPa |  | р = 2.8 MPa |  |
| 230 | 0.07796 | 2814.2 | 0.07455 | 2808.0 | - | - |
| 240 | 0.08066 | 2845.6 | 0.07721 | 2840.1 | 0.07399 | 2834.5 |
| 250 | 0.08323 | 2875.1 | 0.07973 | 2870.3 | 0.07647 | 2865.3 |
| 260 | 0.08570 | 2903.2 | 0.08214 | 2898.9 | 0.07883 | 2894.5 |
| 270 | 0.08807 | 2930.2 | 0.08445 | 2926.3 | 0.08110 | 2922.3 |
| 280 | 0.09037 | 2956.3 | 0.08670 | 2952.7 | 0.08329 | 2949.1 |
| 290 | 0.09262 | 2981.6 | 0.08889 | 2978.4 | 0.08542 | 2975.1 |
| 300 | 0.09482 | 3006.4 | 0.09103 | 3003.4 | 0.08751 | 3000.4 |
| 310 | 0.09698 | 3030.7 | 0.09313 | 3027.9 | 0.08955 | 3025.1 |
| 320 | 0.09911 | 3054.6 | 0.09519 | 3051.9 | 0.09155 | 3049.3 |
| 330 | 0.10120 | 3078.1 | 0.09722 | 3075.6 | 0.09353 | 3073.2 |
| 340 | 0.10327 | 3101.3 | 0.09923 | 3099.0 | 0.09547 | 3096.7 |
| 350 | 0.10530 | 3124.5 | 0.10121 | 3122.3 | 0.09740 | 3120.1 |
| 360 | 0.10730 | 3147.5 | 0.10318 | 3145.5 | 0.09930 | 3143.4 |
| 370 | 0.10930 | 3170.4 | 0.10510 | 3168.5 | 0.10118 | 3166.6 |
| 380 | 0.11130 | 3193.2 | 0.10700 | 3191.3 | 0.10305 | 3189.5 |
| 390 | 0.11330 | 3215.8 | 0.10890 | 3214.0 | 0.10490 | 3212.3 |
| 400 | 0.11530 | 3238.3 | 0.11080 | 3236.6 | 0.10670 | 3234.9 |
| 410 | 0.11720 | 3260.6 | 0.11270 | 3259.0 | 0.10860 | 3257.5 |
| 420 | 0.11920 | 3283.0 | 0.11460 | 3281.4 | 0.11040 | 3279.9 |
| 430 | 0.12110 | 3305.2 | 0.11650 | 3303.8 | 0.11220 | 3302.3 |
| 440 | 0.12300 | 3327.5 | 0.11830 | 3326.1 | 0.11400 | 3324.7 |
| 450 | 0.12500 | 3349.7 | 0.12020 | 3348.4 | 0.11580 | 3347.0 |
| 460 | 0.12690 | 3371.9 | 0.12200 | 3370.6 | 0.11760 | 3369.4 |
| 470 | 0.12880 | 3394.1 | 0.12390 | 3392.9 | 0.11930 | 3391.7 |
| 480 | 0.13070 | 3416.4 | 0.12570 | 3415.2 | 0.12110 | 3414.0 |
| 490 | 0.13260 | 3438.6 | 0.12750 | 3437.4 | 0.12290 | 3436.3 |
| 500 | 0.13440 | 3460.8 | 0.12940 | 3459.7 | 0.12460 | 3458.6 |
| 510 | 0.13630 | 3483.1 | 0.13120 | 3482.0 | 0.12640 | 3480.9 |
| 520 | 0.13820 | 3505.4 | 0.13300 | 3504.3 | 0.12810 | 3503.3 |
| 530 | 0.14010 | 3527.7 | 0.13480 | 3526.7 | 0.12990 | 3525.7 |
| 540 | 0.14190 | 3550.0 | 0.13660 | 3549.0 | 0.13160 | 3548.1 |
| 550 | 0.14380 | 3572.4 | 0.13840 | 3571.4 | 0.13330 | 3570.5 |
| 560 | 0.14560 | 3594.8 | 0.14020 | 3593.8 | 0.13510 | 3592.9 |
| 570 | 0.14750 | 3617.2 | 0.14200 | 3616.3 | 0.13680 | 3615.4 |
| 580 | 0.14930 | 3639.7 | 0.14370 | 3638.8 | 0.13850 | 3638.0 |
| 590 | 0.15120 | 3662.2 | 0.14560 | 3661.3 | 0.14020 | 3660.5 |
| 600 | 0.15300 | 3684.7 | 0.14730 | 3683.9 | 0.14200 | 3683.1 |
| 610 | 0.15490 | 3707.2 | 0.14910 | 3706.5 | 0.14370 | 3705.7 |
| 620 | 0.15670 | 3729.9 | 0.15080 | 3729.1 | 0.14540 | 3728.3 |
| 630 | 0.15860 | 3752.5 | 0.15260 | 3751.8 | 0.14710 | 3751.0 |
| 1640 | 0.16040 | 3775.2 | 0.15440 | 3774.5 | 0.14880 | 3773.8 |
| 650 | 0.16220 | 3797.9 | 0.15620 | 3797.2 | 0.15050 | 3796.5 |
|  | р = 2.9 MPa |  | р = 3.0 MPa |  | р = 3.1 MPa |  |
| 240 | 0.07099 | 2828.8 | 0.06818 | 2823.0 | 0.06554 | 2817.0 |
| 250 | 0.07343 | 2860.3 | 0.07058 | 2855.2 | 0.06791 | 2850.0 |
| 260 | 0.07574 | 2890.0 | 0.07286 | 2885.5 | 0.07016 | 2880.8 |
| 270 | 0.07796 | 2918.3 | 0.07504 | 2914.2 | 0.07230 | 2910.0 |
| 280 | 0.08011 | 2945.4 | 0.07714 | 2941.8 | 0.07436 | 2938.0 |
| 290 | 0.08219 | 2971.7 | 0.07918 | 2968.4 | 0.07635 | 2964.9 |
| 300 | 0.08422 | 2997.3 | 0.08116 | 2994.2 | 0.07829 | 2991.0 |
| 310 | 0.08621 | 3022.2 | 0.08310 | 3019.3 | 0.08018 | 3016.4 |
| 320 | 0.08816 | 3046.7 | 0.08500 | 3044.0 | 0.08204 | 3041.3 |
| 330 | 0.09008 | 3070.7 | 0.08687 | 3068.2 | 0.08386 | 3065.7 |
| 340 | 0.09198 | 3094.4 | 0.08871 | 3092.1 | 0.08565 | 3089.7 |
| 350 | 0.09385 | 3118.0 | 0.09053 | 3115.7 | 0.08742 | 3113.5 |
| 360 | 0.09569 | 3141.4 | 0.09232 | 3139.3 | 0.08917 | 3137.3 |
| 370 | 0.09752 | 3164.6 | 0.09410 | 3162.7 | 0.09090 | 3160.7 |
| 380 | 0.09933 | 3187.7 | 0.09586 | 3185.8 | 0.09261 | 3184.0 |
| 390 | 0.10113 | 3210.5 | 0.09760 | 3208.8 | 0.09432 | 3207.0 |
| 400 | 0.10291 | 3233.3 | 0.09933 | 3231.6 | 0.09599 | 3229.9 |
| 410 | 0.10470 | 3255.9 | 0.10105 | 3254.3 | 0.09766 | 3252.7 |
| 420 | 0.10640 | 3278.4 | 0.10276 | 3276.9 | 0.09932 | 3275.3 |
| 430 | 0.10820 | 3300.9 | 0.10450 | 3299.4 | 0.10097 | 3297.9 |
| 440 | 0.10990 | 3323.3 | 0.10610 | 3321.9 | 0.10261 | 3320.5 |
| 450 | 0.11170 | 3345.7 | 0.10780 | 3344.4 | 0.10420 | 3343.0 |
| 460 | 0.11340 | 3368.0 | 0.10950 | 3366.8 | 0.10590 | 3365.5 |
| 470 | 0.11510 | 3390.4 | 0.11120 | «89.2 | 0.10750 | 3387.9 |
| 480 | 0.11680 | 3412.8 | 0.11280 | 34П.6 | 0.10910 | 3410.4 |
| 490 | 0.11850 | 3435.1 | 0.11450 | 3434.0 | 0.11070 | 3432.8 |
| 500 | 0.12020 | 3457.5 | 0.11610 | 3456.4 | 0.11230 | 3455.3 |
| 510 | 0.12190 | 3479.9 | 0.11780 | 3478.8 | 0.11390 | 3477.7 |
| 520 | 0.12360 | 3502.3 | 0.11940 | 3501.2 | 0.11550 | 3500.2 |
| 530 | 0.12530 | 3524.7 | 0.12100 | 3523.7 | 0.11710 | 3522.7 |
| 540 | 0.12700 | 3547.1 | 0.12270 | 3546.1 | 0.11860 | 3545.2 |
| 550 | 0.12870 | 3569.5 | 0.12430 | 3568.6 | 0.12020 | 3567.7 |
| 560 | 0.13030 | 3592.0 | 0.12590 | 3591.1 | 0.12180 | 3590.2 |
| 570 | 0.13200 | 3614.6 | 0.12750 | 3613.7 | 0.12340 | 3612.8 |
| 580 | 0.13360 | 3637.1 | 0.12920 | 3636.3 | 0.12490 | 3635.4 |
| 590 | 0.13530 | 3659.7 | 0.13080 | 3658.9 | 0.12650 | 3658.0 |
| 600 | 0.13700 | 3682.3 | 0.13240 | 3681.5 | 0.12800 | 3680.7 |
| 610 | 0.13870 | 3704.9 | 0.13400 | 3704.1 | 0.12960 | 3703.4 |
| 620 | 0.14030 | 3727.6 | 0.13560 | 3726.8 | 0.13120 | 3726.1 |
| 630 | 0.14200 | 3750.3 | 0.13720 | 3749.6 | 0.13270 | 3748.8 |
| 640 | 0.14360 | 3773.0 | 0.13880 | 3772.3 | 0.13420 | 3771.6 |
| 650 | 0.14530 | 3795.8 | 0.14040 | 3795.1 | 0.13580 | 3794.4 |
|  | р = 3.2 MPa |  | р = 3.3 MPa |  | р = 3.4 MPa |  |
| 240 | 0.06306 | 2810.9 | 0.06072 | 2804.7 | - | - |
| 250 | 0.06540 | 2844.7 | 0.06305 | 2839.3 | 0.06082 | 2833.8 |
| 260 | 0.06762 | 2876.2 | 0.06523 | 2871.4 | 0.06298 | 2866.5 |
| 270 | 0.06973 | 2905.9 | 0.06730 | 2901.6 | 0.06502 | 2897.3 |
| 280 | 0.07175 | 2934.2 | 0.06929 | 2930.4 | 0.06698 | 2926.5 |
| 290 | 0.07370 | 2961.5 | 0.07121 | 2958.0 | 0.06886 | 2954.5 |
| 300 | 0.07560 | 2987.9 | 0.07307 | 2984.7 | 0.07068 | 2981.5 |
| 310 | 0.07745 | 3013.5 | 0.07488 | 3010.6 | 0.07246 | 3007.6 |
| 320 | 0.07926 | 3038.6 | 0.07665 | 3035.9 | 0.07419 | 3033.1 |
| 330 | 0.08104 | 3063.2 | 0.07839 | 3060.6 | 0.07589 | 3058.0 |
| 340 | 0.08279 | 3087.4 | 0.08010 | 3085.0 | 0.07756 | 3082.6 |
| 350 | 0.08452 | 3111.3 | 0.08178 | 3109.1 | 0.07920 | 3106.8 |
| 360 | 0.08622 | 3135.2 | 0.08344 | 3133.2 | 0.08083 | 3131.0 |
| 370 | 0.08790 | 3158.7 | 0.08508 | 3156.8 | 0.08243 | 3154.8 |
| 380 | 0.08956 | 3182.1 | 0.08670 | 3180.2 | 0.08401 | 3178.3 |
| 390 | 0.09121 | 3205.2 | 0.08831 | 3203.5 | 0.08557 | 3201.7 |
| 400 | 0.09280 | 3228.2 | 0.08990 | 3226.5 | 0.08713 | 3224.8 |
| 410 | 0.09447 | 3251.1 | 0.09148 | 3249.5 | 0.08867 | 3247.8 |
| 420 | 0.09609 | 3273.8 | 0.09305 | 3272.3 | 0.09020 | 3270.7 |
| 430 | 0.09769 | 3296.5 | 0.09461 | 3295.0 | 0.09172 | 3293.5 |
| 440 | 0.09929 | 3319.1 | 0.09617 | 3317.7 | 0.09323 | 3316.3 |
| 450 | 0.10087 | 3341.6 | 0.09771 | 3340.3 | 0.09473 | 3338.9 |
| 460 | 0.10245 | 3364.2 | 0.09924 | 3362.9 | 0.09622 | 3361.6 |
| 470 | 0.10400 | 3386.7 | 0.10077 | 3385.4 | 0.09771 | 3384.2 |
| 480 | 0.10560 | 3409.2 | 0.10229 | 3408.0 | 0.09919 | 3406.8 |
| 490 | 0.10710 | 3431.7 | 0.10380 | 3430.5 | 0.10067 | 3429.4 |
| 500 | 0.10870 | 3454.2 | 0.10530 | 3453.0 | 0.10213 | 3451.9 |
| 510 | 0.11020 | 3476.6 | 0.10680 | 3475.6 | 0.10360 | 3474.5 |
| 520 | 0.11180 | 3499.1 | 0.10830 | 3498.1 | 0.10510 | 3497.1 |
| 530 | 0.11330 | 3521.6 | 0.10980 | 3520.6 | 0.10650 | 3519.6 |
| 540 | 0.11490 | 3544.2 | 0.11130 | 3543.2 | 0.10800 | 3542.2 |
| 550 | 0.11640 | 3566.7 | 0.11280 | 3565.8 | 0.10940 | 3564.8 |
| 560 | 0.11790 | 3589.3 | 0.11430 | 3588.4 | 0.11080 | 3587.5 |
| 570 | 0.11940 | 3611.9 | 0.11570 | 3611.0 | 0.11230 | 3610.2 |
| 580 | 0.12090 | 3634.6 | 0.11720 | 3633.7 | 0.11370 | 3632.8 |
| 590 | 0.12250 | 3657.2 | 0.11870 | 3656.4 | 0.11510 | 3655.6 |
| 600 | 0.12400 | 3679.9 | 0.12020 | 3679.1 | 0.11660 | 3678.3 |
| 610 | 0.12550 | 3702.6 | 0.12160 | 3701.8 | 0.11800 | 3701.0 |
| 620 | 0.12700 | 3725.3 | 0.12310 | 3724.6 | 0.11940 | 3723.8 |
| 630 | 0.12850 | 3748.1 | 0.12450 | 3747.3 | 0.12080 | 3746.6 |
| 640 | 0.13000 | 3770.9 | 0.12600 | 3770.2 | 0.12220 | 3769.4 |
| 650 | 0.13150 | 3793.7 | 0.12750 | 3793.0 | 0.12370 | 3792.3 |
|  | р = 3.5 MPa |  | р = 3.6 MPa |  | р = 3.7 MPa |  |
| 250 | 0.05871 | 2828.1 | 0.05671 | 2822.4 | 0.05482 | 2816.5 |
| 260 | 0.06085 | 2861.6 | 0.05883 | 2856.6 | 0.05692 | 2851.5 |
| 270 | 0.06287 | 2892.9 | 0.06083 | 2888.5 | 0.05890 | 2884.0 |
| 280 | 0.06479 | 2922.6 | 0.06273 | 2918.6 | 0.06077 | 2914.6 |
| 290 | 0.06664 | 2950.9 | 0.06455 | 2947.3 | 0.06256 | 2943.7 |
| 300 | 0.06843 | 2978.2 | 0.06631 | 2974.9 | 0.06429 | 2971.6 |
| 310 | 0.07017 | 3004.6 | 0.06802 | 3001.6 | 0.06597 | 2998.6 |
| 320 | 0.07187 | 3030.3 | 0.06968 | 3027.6 | 0.06761 | 3024.7 |
| 330 | 0.07354 | 3055.5 | 0.07131 | 3052.9 | 0.06920 | 3050.3 |
| 340 | 0.07517 | 3080.2 | 0.07291 | 3077.7 | 0.07077 | 3075.3 |
| 350 | 0.07678 | 3104.6 | 0.07448 | 3102.3 | 0.07231 | 3100.0 |
| 360 | 0.07836 | 3128.9 | 0.07603 | 3126.8 | 0.07383 | 3124.6 |
| 370 | 0.07992 | 3152.8 | 0.07756 | 3150.8 | 0.07532 | 3148.8 |
| 380 | 0.08146 | 3176.4 | 0.07907 | 3174.6 | 0.07680 | 3172.7 |
| 390 | 0.08300 | 3199.9 | 0.08056 | 3198.1 | 0.07826 | 3196.9 |
| 400 | 0.08451 | 3223.1 | 0.08204 | 3221.4 | 0.07970 | 3219.7 |
| 410 | 0.08602 | 3246.2 | 0.08351 | 3244.6 | 0.08114 | 3243.0 |
| 420 | 0.08751 | 3269.2 | 0.08496 | 3267.7 | 0.08256 | 3266.1 |
| 430 | 0.08899 | 3292.0 | 0.08641 | 3290.6 | 0.08397 | 3389.1 |
| 440 | 0.09046 | 3314.8 | 0.08784 | 3313.4 | 0.08537 | 3312.9 |
| 450 | 0.09192 | 3337.6 | 0.08927 | 3336.2 | 0.08676 | 3334.4 |
| 460 | 0.09338 | 3360.3 | 0.09069 | 3359.0 | 0.08815 | 3357.7 |
| 470 | 0.09483 | 3382.9 | 0.09210 | 3381.7 | 0.08953 | 3380.4 |
| 480 | 0.09627 | 3405.6 | 0.09351 | 3404.4 | 0.09090 | 3403.2 |
| 490 | 0.09770 | 3428.2 | 0.09491 | 3427.0 | 0.09226 | 3425.9 |
| 500 | 0.09913 | 3450.8 | 0.09630 | 3449.7 | 0.09362 | 3448.6 |
| 510 | 0.10056 | 3473.4 | 0.09769 | 3472.3 | 0.09497 | 3471.2 |
| 520 | 0.10198 | 3496.0 | 0.09907 | 3495.0 | 0.09632 | 3493.9 |
| 530 | 0.10340 | 3518.6 | 0.10045 | 3517.6 | 0.09767 | 3516.6 |
| 540 | 0.10480 | 3541.3 | 0.10182 | 3540.3 | 0.09901 | 3539.3 |
| 550 | 0.10620 | 3563.9 | 0.10320 | 3563.0 | 0.10034 | 3562.0 |
| 560 | 0.10760 | 3586.6 | 0.10460 | 3585.7 | 0.10167 | 3584.8 |
| 570 | 0.10900 | 3609.3 | 0.10590 | 3608.4 | 0.10300 | 3607.5 |
| 580 | 0.11040 | 3632.0 | 0.10730 | 3631.1 | 0.10430 | 3630.3 |
| 590 | 0.11180 | 3654.7 | 0.10860 | 3653.9 | 0.10560 | 3653.1 |
| 600 | 0.11320 | 3677.5 | 0.11000 | 3676.7 | 0.10700 | 3675.9 |
| 610 | 0.11460 | 3700.2 | 0.11130 | 3699.4 | 0.10830 | 3698.7 |
| 620 | 0.11600 | 3723.0 | 0.11270 | 3722.3 | 0.10960 | 3721.5 |
| 630 | 0.11730 | 3745.8 | 0.11400 | 3745.1 | 0.11090 | 3744.4 |
| 640 | 0.11870 | 3768.7 | 0.11540 | 3768.0 | 0.11220 | 3767.3 |
| 650 | 0.12010 | 3791.6 | 0.11670 | 3790.9 | 0.11350 | 3790.2 |
|  | р = 3.8 MPa |  | р = 3.9 MPa |  | р = 4.0 MPa |  |
| 250 | 0.05302 | 2810.5 | 0.05130 | 2804.4 | - | - |
| 260 | 0.05511 | 2846.3 | 0.05338 | 2841.0 | 0.05174 | 2835.6 |
| 270 | 0.05706 | 2879.4 | 0.05532 | 2874.8 | 0.05366 | 2870.1 |
| 280 | 0.05891 | 2910.5 | 0.05715 | 2906.4 | 0.05547 | 2902.2 |
| 290 | 0.06068 | 2940.0 | 0.05889 | 2936.3 | 0.05719 | 2932.5 |
| 300 | 0.06238 | 2968.3 | 0.06057 | 2964.9 | 0.05885 | 2961.5 |
| 310 | 0.06403 | 2995.5 | 0.06220 | 2992.4 | 0.06045 | 2989.2 |
| 320 | 0.06564 | 3021.9 | 0.06377 | 3019.1 | 0.06200 | 3016.2 |
| 330 | 0.06721 | 3047.6 | 0.06531 | 3045.0 | 0.06351 | 3042.3 |
| 340 | 0.06875 | 3072.8 | 0.06682 | 3070.4 | 0.06499 | 3067.9 |
| 350 | 0.07026 | 3097.7 | 0.06830 | 3095.4 | 0.06645 | 3093.1 |
| 360 | 0.07174 | 3122.5 | 0.06976 | 3120.0 | 0.06787 | 3118.2 |
| 370 | 0.07320 | 3146.7 | 0.07119 | 3144.7 | 0.06928 | 3142.7 |
| 380 | 0.07465 | 3170.7 | 0.07260 | 3168.8 | 0.07066 | 3166.9 |
| 390 | 0.07670 | 3195.5 | 0.07400 | 3192.7 | 0.07203 | 3190.8 |
| 400 | 0.07749 | 3218.0 | 0.07538 | 3216.3 | 0.07339 | 3214.5 |
| 410 | 0.07889 | 3241.3 | 0.07676 | 3239.7 | 0.07473 | 3238.0 |
| 420 | 0.08028 | 3264.5 | 0.07811 | 3262.9 | 0.07606 | 3261.4 |
| 430 | 0.08166 | 3287.6 | 0.07946 | 3286.1 | 0.07738 | 3284.6 |
| 440 | 0.08303 | 3310.6 | 0.08080 | 3309.1 | 0.07869 | 3307.7 |
| 450 | 0.08439 | 3333.5 | 0.08213 | 3332.1 | 0.07999 | 3330.7 |
| 460 | 0.08574 | 3356.3 | 0.08345 | 3355.0 | 0.08128 | 3353.7 |
| 470 | 0.08708 | 3379.1 | 0.08477 | 3377.9 | 0.08257 | 3376.6 |
| 480 | 0.08842 | 3401.9 | 0.08607 | 3400.7 | 0.08384 | 3399.5 |
| 490 | 0.08975 | 3424.7 | 0.08737 | 3423.5 | 0.08512 | 3422.3 |
| 500 | 0.09108 | 3447.4 | 0.08867 | 3446.3 | 0.08638 | 3445.2 |
| 5Ю | 0.09240 | 3470.2 | 0.08996 | 3469.1 | 0.08764 | 3468.0 |
| 520 | 0.09372 | 3492.9 | 0.09125 | 3491.8 | 0.08890 | 3490.8 |
| 530 | 0.09503 | 3515.6 | 0.09253 | 3514.6 | 0.09015 | 3513.6 |
| 540 | 0.09634 | 3538.3 | 0.09380 | 3537.3 | 0.09140 | 3536.4 |
| 550 | 0.09764 | 3561.0 | 0.09507 | 3560. 1 | 0.09264 | 3559.2 |
| 560 | 0.09893 | 3583.8 | 0.09634 | 3582.9 | 0.09387 | 3582.0 |
| 570 | 0.10023 | 3606.6 | 0.09760 | 3605.8 | 0.09510 | 3604.9 |
| 580 | 0.10152 | 3629.4 | 0.09886 | 3628.6 | 0.09634 | 3627.7 |
| 590 | 0.10280 | 3652.2 | 0.10012 | 3651.4 | 0.09756 | 3650.6 |
| 600 | 0.10410 | 3675.1 | 0.10137 | 3674.2 | 0.09879 | 3673.4 |
| 610 | 0.10540 | 3697.9 | 0.10260 | 3697.1 | 0.10001 | 3696.3 |
| 620 | 0.10660 | 3720.7 | 0.10390 | 3720.0 | 0.10123 | 3719.2 |
| 630 | 0.10790 | 3743.6 | 0.10510 | 3742.9 | 0.10245 | 3742.2 |
| 640 | 0.10920 | 3766.6 | 0.10640 | 3765.8 | 0.10370 | 3765.1 |
| 650 | 0.11050 | 3789.5 | 0.10760 | 3788.8 | 0.10490 | 3788.1 |
|  | р = 4.1 MPa |  | р = 4.2 MPa |  | р = 4.3 MPa |  |
| 260 | 0.05017 | 2830.2 | 0.04867 | 2824.6 | 0.04723 | 2818.9 |
| 270 | 0.05208 | 2865.3 | 0.05056 | 2860.4 | 0.04912 | 2855.5 |
| 280 | 0.05387 | 2898.0 | 0.05234 | 2893.7 | 0.05089 | 2889.3 |
| 290 | 0.05558 | 2928.7 | 0.05403 | 2924.9 | 0.05256 | 2921.0 |
| 300 | 0.05721 | 2958.0 | 0.05564 | 2954.6 | 0.05415 | 2951.0 |
| 310 | 0.05878 | 2986.2 | 0.05720 | 2983.0 | 0.05568 | 2979.8 |
| 320 | 0.60310 | 3013.3 | 0.05870 | 3010.4 | 0.05717 | 3007.4 |
| 330 | 0.06180 | 3039.6 | 0.06017 | 3036.9 | 0.05861 | 3034.2 |
| 340 | 0.06325 | 3065.4 | 0.06160 | 3062.9 | 0.06002 | 3060.4 |
| 350 | 0.06468 | 3090.8 | 0.06300 | 3088.4 | 0.06139 | 3086.1 |
| 360 | 0.06608 | 3116.0 | 0.06437 | 3113.8 | 0.06275 | 3111.6 |
| 370 | 0.06746 | 3140.6 | 0.06573 | 3138.6 | 0.06407 | 3136.5 |
| 380 | 0.06882 | 3165.0 | 0.06706 | 3163.0 | 0.06538 | 3161.1 |
| 390 | 0.07016 | 3189.0 | 0.06838 | 3187.2 | 0.06667 | 3185.3 |
| 400 | 0.07149 | 3212.8 | 0.06968 | 3211.1 | 0.06795 | 3209.3 |
| 410 | 0.07280 | 3236.4 | 0.07097 | 3234.7 | 0.06921 | 3233.1 |
| 420 | 0.07410 | 3259.8 | 0.07224 | 3258.2 | 0.07047 | 3256.6 |
| 430 | 0.07540 | 3283.1 | 0.07351 | 3281.6 | 0.07171 | 3280.1 |
| 440 | 0.07668 | 3306.3 | 0.07476 | 3304.8 | 0.07294 | 3303.4 |
| 450 | 0.07795 | 3329.4 | 0.07601 | 3328.0 | 0.07416 | 3326.6 |
| 460 | 0.07921 | 3352.4 | 0.07725 | 3351.1 | 0.07537 | 3349.7 |
| 470 | 0.08047 | 3375.4 | 0.07848 | 3374.1 | 0.07658 | 3372.8 |
| 480 | 0.08172 | 3398.3 | 0.07970 | 3397.1 | 0.07778 | 3395.8 |
| 490 | 0.08297 | 3421.2 | 0.08092 | 3420.0 | 0.07897 | 3418.8 |
| 500 | 0.08421 | 3444.0 | 0.08213 | 3442.9 | 0.08015 | 3441.8 |
| 510 | 0.08544 | 3466.9 | 0.08334 | 3465.8 | 0.08133 | 3464.7 |
| 520 | 0.08667 | 3489.7 | 0.08454 | 3488.7 | 0.08251 | 3487.6 |
| 530 | 0.08789 | 3512.6 | 0.08574 | 3511.5 | 0.08368 | 3510.5 |
| 540 | 0.08911 | 3535.4 | 0.08694 | 3534.4 | 0.08485 | 3533.4 |
| 550 | 0.09032 | 3558.2 | 0.08812 | 3557.2 | 0.08601 | 3556.3 |
| 560 | 0.09152 | 3581.1 | 0.08929 | 3580.2 | 0.08716 | 3579.2 |
| 570 | 0.09273 | 3604.0 | 0.09047 | 3603.1 | 0.08832 | 3602.2 |
| 580 | 0.09394 | 3626.9 | 0.09165 | 3626.0 | 0.08947 | 3625.1 |
| 590 | 0.09514 | 3649.7 | 0.09282 | 3648.9 | 0.09062 | 3648.1 |
| 600 | 0.09633 | 3672.6 | 0.09399 | 3671.8 | 0.09176 | 3671.0 |
| 610 | 0.09753 | 3695.5 | 0.09516 | 3694.8 | 0.09290 | 3694.0 |
| 620 | 0.09872 | 3718.4 | 0.09633 | 3717.7 | 0.09404 | 3716.9 |
| 630 | 0.09991 | 3741.4 | 0.09749 | 3740.7 | 0.09518 | 3739.9 |
| 640 | 0.10110 | 3764.4 | 0.09865 | 3763.7 | 0.09632 | 3762.9 |
| 650 | 0.10228 | 3787.4 | 0.09981 | 3786.7 | 0.09745 | 3786.0 |
|  | р = 4.4 MPa |  | р = 4.5 MPa |  | р = 4.6 MPa |  |
| 260 | 0.04585 | 2813.0 | 0.04454 | 2807.1 | 0.04327 | 2801.0 |
| 270 | 0.04774 | 2850.4 | 0.04641 | 2845.3 | 0.04514 | 2840.1 |
| 280 | 0.04949 | 2884.9 | 0.04816 | 2880.4 | 0.04688 | 2875.8 |
| 290 | 0.05115 | 2917.1 | 0.04980 | 2913.1 | 0.04850 | 2909.0 |
| 300 | 0.05272 | 2947.5 | 0.05136 | 2943.9 | 0.05005 | 2940.3 |
| 310 | 0.05424 | 2976.5 | 0.05285 | 2973.3 | 0.05153 | 2970.0 |
| 320 | 0.05570 | 3004.5 | 0.05430 | 3001.5 | 0.05295 | 2998.5 |
| 330 | 0.05712 | 3031.5 | 0.05570 | 3028.7 | 0.05434 | 3026.0 |
| 340 | 0.05851 | 3057.8 | 0.05706 | 3055.3 | 0.05568 | 3052.7 |
| 350 | 0.05986 | 3083.7 | 0.05840 | 3081.3 | 0.05700 | 3078.9 |
| 360 | 0.06119 | 3109.4 | 0.05971 | 3107.2 | 0.05828 | 3105.0 |
| 370 | 0.06250 | 3134.4 | 0.06099 | 3132.3 | 0.05955 | 3130.2 |
| 380 | 0.06378 | 3159.1 | 0.06225 | 3157.1 | 0.06079 | 3155.2 |
| 390 | 0.06505 | 3183.5 | 0.06350 | 3181.6 | 0.06201 | 3179.8 |
| 400 | 0.06630 | 3207.6 | 0.06473 | 3205.8 | 0.06322 | 3204.0 |
| 410 | 0.06754 | 3231.4 | 0.06595 | 3229.7 | 0.06442 | 3228.0 |
| 420 | 0.06877 | 3255.1 | 0.06715 | 3253.5 | 0.06560 | 3251.9 |
| 430 | 0.06999 | 3278.6 | 0.06834 | 3277.0 | 0.06677 | 3275.5 |
| 440 | 0.07119 | 3301.9 | 0.06953 | 3300.5 | 0.06793 | 3299.0 |
| 450 | 0.07239 | 3325.2 | 0.07070 | 3323.8 | 0.06909 | 3322.4 |
| 460 | 0.07358 | 3348.4 | 0.07187 | 3347.1 | 0.07023 | 3345.7 |
| 470 | 0.07476 | 3371.5 | 0.07303 | 3370.3 | 0.07137 | 3369.0 |
| 480 | 0.07594 | 3394.6 | 0.07418 | 3393.4 | 0.07250 | 3392.2 |
| 490 | 0.07710 | 3417.6 | 0.07532 | 3416.5 | 0.07362 | 3415.3 |
| 500 | 0.07827 | 3440.6 | 0.07646 | 3439.5 | 0.07474 | 3438.4 |
| 510 | 0.07942 | 3463.6 | 0.07760 | 3462.5 | 0.07585 | 3461.4 |
| 520 | 0.08057 | 3486.8 | 0.07872 | 3485.5 | 0.07696 | 3484.4 |
| 530 | 0.08172 | 3509.5 | 0.07985 | 3508.5 | 0.07806 | 3507.5 |
| 540 | 0.08286 | 3532.4 | 0.08097 | 3531.4 | 0.07915 | 3530.5 |
| 550 | 0.08400 | 3555.4 | 0.08208 | 3554.4 | 0.08024 | 3553.5 |
| 560 | 0.08513 | 3578.5 | 0.08319 | 3577.4 | 0.08133 | 3576.5 |
| 570 | 0.08626 | 3601.3 | 0.08429 | 3600.4 | 0.08241 | 3599.5 |
| 580 | 0.08739 | 3624.3 | 0.08540 | 3623.4 | 0.08350 | 3622.6 |
| 590 | 0.08851 | 3647.2 | 0.08650 | 3646.4 | 0.08457 | 3645.6 |
| 600 | 0.08963 | 3670.2 | 0.08760 | 3669.4 | 0.08565 | 3668.6 |
| 610 | 0.09075 | 3693.2 | 0.08869 | 3692.4 | 0.08672 | 3691.6 |
| 620 | 0.09186 | 3716.2 | 0.08978 | 3715.4 | 0.08779 | 3714.6 |
| 630 | 0.09298 | 3739.2 | 0.09087 | 3738.4 | 0.08886 | 3737.7 |
| 640 | 0.09409 | 3762.2 | 0.09196 | 3761.5 | 0.08992 | 3760.8 |
| 650 | 0.09520 | 3785.3 | 0.09304 | 3784.6 | 0.09099 | 3783.9 |
|  | р = 4.7 MPa |  | р = 4.8 MPa |  | р = 4.9 MPa |  |
| 270 | 0.04392 | 2834.8 | 0.04274 | 2829.4 | 0.04162 | 2824.0 |
| 280 | 0.04565 | 2871.2 | 0.04447 | 2866.6 | 0.04333 | 2861.8 |
| 290 | 0.04726 | 2904.9 | 0.04607 | 2900.8 | 0.04493 | 2896.6 |
| 300 | 0.04879 | 2936.6 | 0.04759 | 2932.9 | 0.04644 | 2929.2 |
| 310 | 0.05026 | 2966.6 | 0.04904 | 2963.3 | 0.04787 | 2959.9 |
| 320 | 0.05167 | 2995.4 | 0.05043 | 2992.4 | 0.04925 | 2989.3 |
| 330 | 0.05303 | 3023.2 | 0.05178 | 3020.4 | 0.05058 | 3017.5 |
| 340 | 0.05436 | 3050.1 | 0.05309 | 3047.5 | 0.05187 | 3044.9 |
| 350 | 0.05565 | 3076.5 | 0.05437 | 3074.1 | 0.05313 | 3071.6 |
| 360 | 0.05692 | 3102.7 | 0.05561 | 3100.5 | 0.05436 | 3098.2 |
| 370 | 0.05816 | 3128.1 | 0.05684 | 3126.0 | 0.05557 | 3123.9 |
| 380 | 0.05939 | 3153.2 | 0.05804 | 3151.2 | 0.05675 | 3149.2 |
| 390 | 0.06059 | 3177.9 | 0.05923 | 3176.0 | 0.05792 | 3174.1 |
| 400 | 0.06178 | 3202.2 | 0.06040 | 3200.5 | 0.05907 | 3198.7 |
| 410 | 0.06295 | 3226.4 | 0.06155 | 3224.7 | 0.06021 | 3223.0 |
| 420 | 0.06412 | 3250.3 | 0.06269 | 3248.7 | 0.06133 | 3247.0 |
| 430 | 0.06527 | 3274.0 | 0.06383 | 3272.4 | 0.06244 | 3270.9 |
| 440 | 0.06641 | 3297.6 | 0.06495 | 3296.1 | 0.06354 | 3294.6 |
| 450 | 0.06754 | 3321.0 | 0.06606 | 3319.6 | 0.06464 | 3318.2 |
| 460 | 0.06866 | 3344.4 | 0.06716 | 3343.1 | 0.06572 | 3341.7 |
| 470 | 0.06978 | 3367.7 | 0.06826 | 3366.4 | 0.06680 | 3365.1 |
| 480 | 0.07089 | 3390.9 | 0.06934 | 3389.7 | 0.06787 | 3388.4 |
| 490 | 0.07199 | 3414.1 | 0.07043 | 3412.9 | 0.06893 | 3411.7 |
| 500 | 0.07309 | 3437.2 | 0.07150 | 3436.1 | 0.06998 | 3434.9 |
| 510 | 0.07418 | 3460.3 | 0.07257 | 3459.2 | 0.07103 | 3458.1 |
| 520 | 0.07526 | 3483.4 | 0.07364 | 3482.3 | 0.07208 | 3481.2 |
| 530 | 0.07634 | 3506.4 | 0.07470 | 3505.4 | 0.07312 | 3504.4 |
| 540 | 0.07742 | 3529.5 | 0.07575 | 3528.5 | 0.07416 | 3527.5 |
| 550 | 0.07849 | 3552.5 | 0.07680 | 3551.5 | 0.07519 | 3550.6 |
| 560 | 0.07955 | 3575.6 | 0.07784 | 3574.6 | 0.07621 | 3573.7 |
| 570 | 0.08061 | 3598.6 | 0.07889 | 3597.7 | 0.07723 | 3596.8 |
| 580 | 0.08167 | 3621.7 | 0.07993 | 3620.8 | 0.07825 | 3620.0 |
| 590 | 0.08273 | 3644.7 | 0.08096 | 3643.9 | 0.07927 | 3643.1 |
| 600 | 0.08378 | 3667.8 | 0.08200 | 3667.0 | 0.08028 | 3666.2 |
| 610 | 0.08484 | 3690.8 | 0.08303 | 3690.0 | 0.08130 | 3689.2 |
| 620 | 0.08588 | 3713.9 | 0.08406 | 3713.1 | 0.08230 | 3712.3 |
| 630 | 0.08693 | 3736.9 | 0.08508 | 3736.2 | 0.08331 | 3735.4 |
| 640 | 0.08797 | 3760.0 | 0.08611 | 3759.3 | 0.08432 | 3758.6 |
| 650 | 0.08902 | 3783.2 | 0.08713 | 3782.5 | 0.08532 | 3781.8 |
|  | р = 5.0 MPa |  | р = 5.2 MPa |  | р = 5.4 MPa |  |
| 270 | 0.04053 | 2818.4 | 0.03847 | 2806.8 | 0.03654 | 2794.8 |
| 280 | 0.04224 | 2857.0 | 0.04018 | 2847.1 | 0.03825 | 2836.8 |
| 290 | 0.04383 | 2892.4 | 0.04175 | 2883.7 | 0.03981 | 2874.8 |
| 300 | 0.04532 | 2925.4 | 0.04322 | 2917.7 | 0.04127 | 2909.8 |
| 310 | 0.04675 | 2956.5 | 0.04462 | 2949.4 | 0.04265 | 2942.5 |
| 320 | 0.04811 | 2986.2 | 0.04596 | 2979.9 | 0.04397 | 2973.5 |
| 330 | 0.04942 | 3014.6 | 0.04725 | 3008.9 | 0.04523 | 3003.0 |
| 340 | 0.05070 | 3042.2 | 0.04849 | 3036.7 | 0.04645 | 3031.5 |
| 350 | 0.05194 | 3069.2 | 0.04971 | 3064.3 | 0.04763 | 3059.3 |
| 360 | 0.05316 | 3095.9 | 0.05089 | 3091.3 | 0.04878 | 3086.7 |
| 370 | 0.05435 | 3121.8 | 0.05204 | 3117.5 | 0.04991 | 3113.1 |
| 380 | 0.05551 | 3147.2 | 0.05318 | 3143.1 | 0.05102 | 3139.1 |
| 390 | 0.05666 | 3172.2 | 0.05430 | 3168.4 | 0.05210 | 3164.5 |
| 400 | 0.05780 | 3196.9 | 0.05541 | 3193.4 | 0.05317 | 3189.7 |
| 410 | 0.05891 | 3221.3 | 0.05648 | 3217.9 | 0.05422 | 3214.4 |
| 420 | 0.06002 | 3245.4 | 0.05755 | 3242.2 | 0.05526 | 3238.9 |
| 430 | 0.06111 | 3269.4 | 0.05861 | 3266.3 | 0.05629 | 3263.2 |
| 440 | 0.06220 | 3293.2 | 0.05966 | 3290.2 | 0.05731 | 3287.2 |
| 450 | 0.06327 | 3316.8 | 0.06070 | 3314.0 | 0.05831 | 3311.2 |
| 460 | 0.06434 | 3340.4 | 0.06173 | 3337.7 | 0.05931 | 3335.0 |
| 470 | 0.06539 | 3363.8 | 0.06275 | 3361.2 | 0.06030 | 3358.6 |
| 480 | 0.06644 | 3387.2 | 0.06377 | 3384.7 | 0.06129 | 3382.2 |
| 490 | 0.06749 | 3410.5 | 0.06478 | 3408.1 | 0.06226 | 3405.7 |
| 510 | 0.06853 | 3433.8 | 0.06578 | 3431.5 | 0.06323 | 3429.2 |
| 510 | 0.06956 | 3457.0 | 0.06677 | 3454.8 | 0.06420 | 3452.6 |
| 520 | 0.07058 | 3480.2 | 0.06777 | 3478.1 | 0.06516 | 3475.9 |
| 530 | 0.07161 | 3503.4 | 0.06875 | 3501.3 | 0.06611 | 3499.2 |
| 540 | 0.07262 | 3526.5 | 0.06974 | 3524.6 | 0.06706 | 3522.5 |
| 550 | 0.07363 | 3549.6 | 0.07071 | 3547.7 | 0.06800 | 3545.8 |
| 560 | 0.07464 | 3572.8 | 0.07168 | 3570.9 | 0.06894 | 3569.1 |
| 570 | 0.07564 | 3596.0 | 0.07265 | 3594.2 | 0.06988 | 3592.4 |
| 500 | 0.07665 | 3619.1 | 0.07362 | 3617.4 | 0.07081 | 3615.6 |
| 590 | 0.07764 | 3642.2 | 0.07458 | 3640.5 | 0.07174 | 3638.9 |
| 600 | 0.07864 | 3665.4 | 0.07554 | 3663.7 | 0.07267 | 3662.1 |
| 610 | 0.07963 | 3688.4 | 0.07650 | 3686.9 | 0.07359 | 3685.3 |
| 620 | 0.08062 | 3711.6 | 0.07745 | 3710.0 | 0.07452 | 3708.5 |
| 630 | 0.08161 | 3734.7 | 0.07840 | 3733.2 | 0.07543 | 3731.7 |
| 640 | 0.08259 | 3757.9 | 0.07935 | 3756.4 | 0.07635 | 3755.0 |
| 650 | 0.08358 | 3781.1 | 0.08030 | 3779.6 | 0.07727 | 3778.2 |
|  | р = 5.6 MPa |  | р = 5.8 MPa |  | р = 6.0 MPa |  |
| 280 | 0.03645 | 2826.3 | 0.03476 | 2815.3 | 0.03317 | 2804.0 |
| 290 | 0.03801 | 2865.6 | 0.03632 | 2856.2 | 0.03473 | 2846.5 |
| 300 | 0.03946 | 2901.7 | 0.03776 | 2893.4 | 0.03616 | 2885.0 |
| 310 | 0.04082 | 2935.3 | 0.03910 | 2927.9 | 0.03750 | 2920.4 |
| 320 | 0.04211 | 2966.9 | 0.04038 | 2960.3 | 0.03876 | 2953.5 |
| 330 | 0.04335 | 2997.1 | 0.04160 | 2991.0 | 0.03996 | 2984.9 |
| 340 | 0.04454 | 3026.0 | 0.04277 | 3020.5 | 0.04111 | 3014.9 |
| 350 | 0.04570 | 3054.2 | 0.04391 | 3049.1 | 0.04223 | 3043.9 |
| 360 | 0.04683 | 3082.0 | 0.04501 | 3077.2 | 0.04331 | 3072.4 |
| 370 | 0.04793 | 3108.7 | 0.04608 | 3104.3 | 0.04436 | 3099.8 |
| 380 | 0.04901 | 3135.0 | 0.04713 | 3130.8 | 0.04538 | 3126.6 |
| 390 | 0.05006 | 3160.7 | 0.04816 | 3156.8 | 0.04639 | 3152.9 |
| 400 | 0.05110 | 3186.0 | 0.04918 | 3182.4 | 0.04738 | 3178.6 |
| 410 | 0.05213 | 3211.0 | 0.05018 | 3207.5 | 0.04835 | 3204.0 |
| 420 | 0.05314 | 3235.6 | 0.05116 | 3232.3 | 0.04931 | 3229.0 |
| 430 | 0.05414 | 3260.1 | 0.05213 | 3256.9 | 0.05026 | 3253.8 |
| 440 | 0.05512 | 3284.3 | 0.05309 | 3281.3 | 0.05119 | 3278.3 |
| 450 | 0.05610 | 3308.3 | 0.05404 | 3305.5 | 0.05212 | 3302.6 |
| 460 | 0.05707 | 3332.2 | 0.05498 | 3329.5 | 0.05303 | 3326.8 |
| 470 | 0.05803 | 3356.0 | 0.05591 | 3353.4 | 0.05394 | 3350.8 |
| 480 | 0.05898 | 3379.7 | 0.05684 | 3377.2 | 0.05484 | 3374.7 |
| 490 | 0.05993 | 3403.3 | 0.05776 | 3400.9 | 0.05573 | 3398.5 |
| 500 | 0.06087 | 3426.9 | 0.05897 | 3424.5 | 0.05662 | 3422.2 |
| 510 | 0.06180 | 3450.3 | 0.05958 | 3448.1 | 0.05750 | 3445.9 |
| 520 | 0.06273 | 3473.8 | 0.06048 | 3471.6 | 0.05837 | 3469.5 |
| 550 | 0.06549 | 3543.8 | 0.06315 | 3541.9 | 0.06096 | 3540.0 |
| 560 | 0.06640 | 3567.2 | 0.06403 | 3565.4 | 0.06182 | 3563.5 |
| 570 | 0.06730 | 3590.6 | 0.06491 | 3588.8 | 0.06267 | 3587.0 |
| 560 | 0.06821 | 3613.9 | 0.06578 | 3612.1 | 0.06352 | 3610.4 |
| 590 | 0.06110 | 3637.2 | 0.06665 | 3635.5 | 0.06436 | 3633.8 |
| 600 | 0.07000 | 3660.4 | 0.06752 | 3658.8 | 0.06521 | 3657.2 |
| 610 | 0.07090 | 3683.7 | 0.06839 | 3682.1 | 0.06604 | 3680.6 |
| 620 | 0.07175 | 3707.0 | 0.06925 | 3705.4 | 0.06688 | 3703.9 |
| 630 | 0.07268 | 3730.2 | 0.07011 | 3728.7 | 0.06772 | 3727.2 |
| 640 | 0.07356 | 3753.5 | 0.07097 | 3752.1 | 0.06855 | 3750.6 |
| 650 | 0.07441 | 3776.8 | 0.07182 | 3775.4 | 0.06938 | 3774.0 |
|  | р = 6.2 MPa |  | р = 6.4 MPa |  | р = 6.6 MPa |  |
| 280 | 0.03166 | 2792.1 | 0.03024 | 2779.8 | - | - |
| 290 | 0.03324 | 2836.5 | 0.03182 | 2826.2 | 0.03049 | 2815.5 |
| 300 | 0.03467 | 2876.3 | 0.03325 | 2867.4 | 0.03192 | 2858.2 |
| 310 | 0.03599 | 2912.7 | 0.03457 | 2904.9 | 0.03324 | 2896.8 |
| 320 | 0.03724 | 2946.0 | 0.03581 | 2939.6 | 0.03446 | 2932.5 |
| 330 | 0.03842 | 2978.6 | 0.03698 | 2972.3 | 0.03562 | 2965.9 |
| 340 | 0.03956 | 3009.2 | 0.03810 | 3003.4 | 0.03673 | 2997.5 |
| 350 | 0.04065 | 3038.6 | 0.03917 | 3033.3 | 0.03779 | 3027.9 |
| 360 | 0.04171 | 3067.7 | 0.04022 | 3062.7 | 0.03881 | 3057.8 |
| 370 | 0.04274 | 3095.3 | 0.04123 | 3090.8 | 0.03980 | 3086.2 |
| 380 | 0.04375 | 3122.4 | 0.04221 | 3118.1 | 0.04077 | 3113.9 |
| 390 | 0.04473 | 3148.9 | 0.04318 | 3144.9 | 0.04171 | 3140.9 |
| 400 | 0.04570 | 3174.9 | 0.04412 | 3171.2 | 0.04263 | 3167.4 |
| 410 | 0.04665 | 3200.5 | 0.04505 | 3196.9 | 0.04354 | 3193.3 |
| 420 | 0.04758 | 3225.7 | 0.04596 | 3222.2 | 0.04444 | 3218.9 |
| 430 | 0.04850 | 3250.6 | 0.04686 | 3247.4 | 0.04532 | 3244.2 |
| 440 | 0.04941 | 3275.2 | 0.04775 | 3272.2 | 0.04618 | 3269.2 |
| 450 | 0.05032 | 3299.7 | 0.04863 | 3296.8 | 0.04704 | 3293.9 |
| 460 | 0.05121 | 3324.0 | 0.04950 | 3321.2 | 0.04789 | 3318.4 |
| 470 | 0.05209 | 3348.1 | 0.05036 | 3345.5 | 0.04873 | 3342.8 |
| 480 | 0.05296 | 3372.2 | 0.05121 | 3369.6 | 0.04956 | 3367.1 |
| 490 | 0.05383 | 3396.1 | 0.05205 | 3393.6 | 0.05038 | 3391.2 |
| 500 | 0.05469 | 3419.9 | 0.05289 | 3417.5 | 0.05120 | 3415.2 |
| 510 | 0.05555 | 3443.6 | 0.05372 | 3441.3 | 0.05201 | 3439.1 |
| 520 | 0.05640 | 3467.3 | 0.05455 | 3465.1 | 0.05282 | 3463.0 |
| 530 | 0.05725 | 3490.9 | 0.05537 | 3488.8 | 0.05362 | 3486.7 |
| 540 | 0.05809 | 3514.5 | 0.05619 | 3512.5 | 0.05441 | 3510.5 |
| 550 | 0.05892 | 3538.0 | 0.05700 | 3536.1 | 0.05520 | 3534.2 |
| 560 | 0.05975 | 3561.6 | 0.05781 | 3559.7 | 0.05599 | 3557.9 |
| 570 | 0.06058 | 3585.2 | 0.05862 | 3583.3 | 0.05677 | 3581.5 |
| 580 | 0.06140 | 3608.6 | 0.05942 | 3606.9 | 0.05755 | 3605.1 |
| 590 | 0.06222 | 3632.1 | 0.06021 | 3630.4 | 0.05833 | 3628.7 |
| 600 | 0.06304 | 3655.5 | 0.06101 | 3653.9 | 0.05910 | 3652.2 |
| 610 | 0.06385 | 3678.9 | 0.06180 | 3677.4 | 0.05987 | 3675.8 |
| 620 | 0.06466 | 3702.3 | 0.06259 | 3700.8 | 0.06064 | 3699.2 |
| 630 | 0.06547 | 3725.7 | 0.06337 | 3724.2 | 0.06140 | 3722.7 |
| 640 | 0.06628 | 3749.2 | 0.06416 | 3747.7 | 0.06216 | 3746.2 |
| 650 | 0.06708 | 3772.6 | 0.06494 | 3771.2 | 0.06292 | 3769.7 |
|  | р = 6.8 MPa |  | р = 7.0 MPa |  | р = 7.2 MPa |  |
| 290 | 0.02922 | 2804.4 | 0.02801 | 2792.9 | 0.02686 | 2780.9 |
| 300 | 0.03066 | 2848.8 | 0.02946 | 2839.2 | 0.02832 | 2829.0 |
| 310 | 0.03197 | 2888.6 | 0.03078 | 2880.2 | 0.02964 | 2871.6 |
| 320 | 0.03319 | 2925.2 | 0.03199 | 2917.8 | 0.03085 | 2910.2 |
| 330 | 0.03434 | 2959.3 | 0.03313 | 2952.6 | 0.03198 | 2945.9 |
| 340 | 0.03543 | 2991.6 | 0.03421 | 2985.5 | 0.03305 | 2979.4 |
| 350 | 0.03647 | 3022.5 | 0.03524 | 3017.0 | 0.03407 | 3011.4 |
| 360 | 0.03748 | 3052.7 | 0.03623 | 3047.6 | 0.03505 | 3042.5 |
| 370 | 0.03846 | 3081.5 | 0.03719 | 3076.8 | 0.02599 | 3072.1 |
| 380 | 0.03941 | 3109.5 | 0.03812 | 3105.2 | 0.03691 | 3100.7 |
| 390 | 0.04033 | 3136.9 | 0.03903 | 3132.8 | 0.03780 | 3128.6 |
| 400 | 0.04124 | 3163.6 | 0.03992 | 3159.7 | 0.03867 | 3155.8 |
| 410 | 0.04213 | 3189.8 | 0.04079 | 3186.1 | 0.03953 | 3182.5 |
| 420 | 0.04300 | 3215.5 | 0.04165 | 3212.1 | 0.04036 | 3208.6 |
| 430 | 0.04386 | 3240.9 | 0.04249 | 3237.7 | 0.04119 | 3234.4 |
| 440 | 0.04471 | 3266.1 | 0.04332 | 3263.0 | 0.04201 | 3259.9 |
| 450 | 0.04555 | 3291.0 | 0.04414 | 3288.0 | 0.04281 | 3285.1 |
| 460 | 0.04637 | 3315.7 | 0.04495 | 3312.8 | 0.04360 | 3310.0 |
| 470 | 0.04719 | 3340.2 | 0.04575 | 3337.5 | 0.04438 | 3334.8 |
| 480 | 0.04800 | 3364.5 | 0.04654 | 3361.9 | 0.04516 | 3359.4 |
| 490 | 0.04881 | 3388.7 | 0.04732 | 3386.3 | 0.04592 | 3383.8 |
| 500 | 0.04961 | 3412.8 | 0.04810 | 3410.5 | 0.04668 | 3408.1 |
| 510 | 0.05040 | 3436.8 | 0.04888 | 3434.5 | 0.04744 | 3432.3 |
| 520 | 0.05118 | 3460.8 | 0.04964 | 3458.6 | 0.04819 | 3456.4 |
| 530 | 0.05196 | 3484.6 | 0.05040 | 3482.5 | 0.04893 | 3480.4 |
| 540 | 0.05274 | 3508.4 | 0.05116 | 3506.4 | 0.04967 | 3504.4 |
| 550 | 0.05351 | 3532.2 | 0.0519) | 3530.2 | 0.05040 | 3528.3 |
| 560 | 0.05427 | 3556.0 | 0.05266 | 3554.1 | 0.05113 | 3552.2 |
| 570 | 0.05504 | 3579.7 | 0.05340 | 3577.9 | 0.05186 | 3576.1 |
| 580 | 0.05580 | 3603.4 | 0.05414 | 3601.6 | 0.05258 | 3599.9 |
| 590 | 0.05655 | 3627.0 | 0.05488 | 3625.3 | 0.05330 | 3623.6 |
| 600 | 0.05730 | 3650.6 | 0.05561 | 3649.0 | 0.05401 | 3647.3 |
| 610 | 0.05805 | 3674.2 | 0.05634 | 3672.6 | 0.05472 | 3671.0 |
| 620 | 0.05880 | 3697.7 | 0.05707 | 3696.2 | 0.05543 | 3694.6 |
| 630 | 0.05954 | 3721.2 | 0.05779 | 3719.7 | 0.05614 | 3718.2 |
| 640 | 0.06028 | 3744.8 | 0.05851 | 3743.3 | 0.05684 | 3741.8 |
| 650 | 0.06102 | 3768.3 | 0.05923 | 3766.9 | 0.05754 | 3765.5 |
|  | р = 7.4 MPa |  | р = 7.6 MPa |  | р = 7.8 MPa |  |
| 290 | 0.02575 | 2768.4 | - | - | - | - |
| 300 | 0.02724 | 2818.7 | 0.02620 | 2808.0 | 0.02520 | 2796.9 |
| 310 | 0.02856 | 2862.7 | 0.02753 | 2853.6 | 0.02654 | 2844.3 |
| 320 | 0.02977 | 2902.4 | 0.02874 | 2894.5 | 0.02775 | 2886.4 |
| 330 | 0.03089 | 2939.0 | 0.02985 | 2931.9 | 0.02887 | 2924.8 |
| 340 | 0.03195 | 2973.2 | 0.03091 | 2966.9 | 0.02991 | 2960.4 |
| 350 | 0.03296 | 3005.8 | 0.03190 | 3000.0 | 0.03090 | 2994.2 |
| 360 | 0.03393 | 3037.3 | 0.03286 | 3032.0 | 0.03185 | 3026.7 |
| 370 | 0.03486 | 3067.3 | 0.03378 | 3062.4 | 0.03276 | 3057.5 |
| 380 | 0.03576 | 3096.3 | 0.03467 | 3091.8 | 0.03364 | 3087.3 |
| 390 | 0.03664 | 3124.5 | 0.03554 | 3120.3 | 0.03449 | 3116.1 |
| 400 | 0.03750 | 3152.0 | 0.03638 | 3148.0 | 0.03532 | 3144.1 |
| 410 | 0.03834 | 3178.8 | 0.03720 | 3175.1 | 0.03613 | 3171.4 |
| 420 | 0.03916 | 3205.2 | 0.03801 | 3201.7 | 0.03692 | 3198.2 |
| 430 | 0.03997 | 3231.2 | 0.03880 | 3227.8 | 0.03770 | 3224.5 |
| 440 | 0.04076 | 3256.8 | 0.03959 | 3253.6 | 0.03847 | 3250.5 |
| 450 | 0.04155 | 3282.1 | 0.04036 | 3279.1 | 0.03922 | 3276.1 |
| 460 | 0.04232 | 3307.2 | 0.04112 | 3304.4 | 0.03997 | 3301.5 |
| 470 | 0.04309 | 3332.1 | 0.04187 | 3329.4 | 0.04070 | 3326.6 |
| 480 | 0.04385 | 3356.8 | 0.0426! | 3354.2 | 0.04143 | 3351.6 |
| 490 | 0.04460 | 3381.3 | 0.04334 | 3378.8 | 0.04215 | 3376.3 |
| 500 | 0.04534 | 3405.7 | 0.04407 | 3403.3 | 0.04286 | 3400.9 |
| 510 | 0.04608 | 3430.0 | 0.04479 | 3427.7 | 0.04357 | 3425.4 |
| 520 | 0.04681 | 3454.2 | 0.04551 | 3452.0 | 0.04427 | 3449.8 |
| 530 | 0.04754 | 3478.3 | 0.04622 | 3476.2 | 0.04496 | 3474.1 |
| 540 | 0.04826 | 3502.3 | 0.04692 | 3500.3 | 0.04565 | 3498.3 |
| 550 | 0.04898 | 3526.3 | 0.04762 | 3524.4 | 0.04634 | 3522.4 |
| 560 | 0.04969 | 3550.3 | 0.04832 | 3548.4 | 0.04702 | 3546.5 |
| 570 | 0.05039 | 3574.2 | 0.04901 | 3572.4 | 0.04770 | 3570.6 |
| 580 | 0.05110 | 3598.1 | 0.04970 | 3596.3 | 0.04837 | 3594.6 |
| 590 | 0.05180 | 3621.9 | 0.05038 | 3620.2 | 0.04904 | 3618.5 |
| 600 | 0.05250 | 3645.6 | 0.05106 | 3644.0 | 0.04970 | 3642.3 |
| 610 | 0.05319 | 3669.4 | 0.05174 | 3667.8 | 0.05037 | 3666.2 |
| 620 | 0.05388 | 3693.0 | 0.05242 | 3691.5 | 0.05103 | 3689.9 |
| 630 | 0.05457 | 3716.7 | 0.05309 | 3715.2 | 0.05168 | 3713.7 |
| 640 | 0.05526 | 3740.3 | 0.05376 | 3738.9 | 0.05234 | 3737.4 |
| 650 | 0.05594 | 3764.0 | 0.05443 | 3762.6 | 0.05299 | 3761.2 |
|  | р = 8.0 MPa |  | р = 8.2 MPa |  | р = 8.4 MPa |  |
| 300 | 0.02425 | 2785.4 | 0.02333 | 2773.5 | 0.02244 | 2760.9 |
| 310 | 0.02560 | 2834.7 | 0.02470 | 2824.8 | 0.02383 | 2814.5 |
| 320 | 0.02682 | 2878.1 | 0.02592 | 2869.6 | 0.02506 | 2860.9 |
| 330 | 0.02793 | 2917.5 | 0.02703 | 2910.0 | 0.02617 | 2902.5 |
| 340 | 0.02897 | 2953.9 | 0.02807 | 2947.3 | 0.02721 | 2940.6 |
| 350 | 0.02995 | 2988.3 | 0.02904 | 2982.3 | 0.02818 | 2976.2 |
| 360 | 0.03089 | 3021.3 | 0.02997 | 3015.8 | 0.02910 | 3010.3 |
| 370 | 0.03179 | 3052.6 | 0.03086 | 3047.6 | 0.02998 | 3042.5 |
| 380 | 0.03265 | 3082.7 | 0.03171 | 3078.1 | 0.03082 | 3073.4 |
| 390 | 0.03349 | 3111.8 | 0.03254 | 3107.5 | 0.03164 | 3103.2 |
| 400 | 0.03431 | 3140.1 | 0.03335 | 3136.1 | 0.03243 | 3132.0 |
| 410 | 0.03511 | 3167.7 | 0.03413 | 3163.9 | 0.03321 | 3160.1 |
| 420 | 0.03589 | 3194.7 | 0.03490 | 3191.1 | 0.03396 | 3187.5 |
| 430 | 0.03665 | 3221.2 | 0.03566 | 3217.8 | 0.03470 | 3214.4 |
| 440 | 0.03741 | 3247.3 | 0.03640 | 3244.1 | 0.03543 | 3240.9 |
| 450 | 0.03815 | 3273.1 | 0.03712 | 3270.1 | 0.03615 | 3267. 1 |
| 460 | 0.03888 | 3298.6 | 0.03784 | 3295.8 | 0.03685 | 3292.9 |
| 470 | 0.03960 | 3323.9 | 0.03855 | 3321.2 | 0.03755 | 3318.4 |
| 480 | 0.04031 | 3349.0 | 0.03925 | 3346.3 | 0.03824 | 3343.7 |
| 490 | 0.04102 | 3373.8 | 0.03994 | 3371.3 | 0.03892 | 3368.8 |
| 500 | 0.04172 | 3398.5 | 0.04062 | 3396.1 | 0.03959 | 3393.7 |
| 510 | 0.04241 | 3423.1 | 0.04130 | 3420.8 | 0.04025 | 3418.5 |
| 520 | 0.04309 | 3447.6 | 0.04197 | 3445.4 | 0.04091 | 3443.1 |
| 530 | 0.04377 | 3471.9 | 0.04264 | 3469.8 | 0.04156 | 3467.7 |
| 540 | 0.04445 | 3496.2 | 0.04330 | 3494.2 | 0.04221 | 3492.1 |
| 550 | 0.04512 | 3520.4 | 0.04396 | 3518.4 | 0.04286 | 3516.4 |
| 560 | 0.04578 | 3544.6 | 0.04461 | 3542.7 | 0.04350 | 3540.8 |
| 570 | 0.04645 | 3568.7 | 0.04526 | 3566.9 | 0.04413 | 3565.0 |
| 580 | 0.04710 | 3592.8 | 0.04590 | 3591.0 | 0.04476 | 3589.2 |
| 590 | 0.04776 | 3616.8 | 0.04654 | 3615.0 | 0.04539 | 3613.3 |
| 600 | 0.04841 | 3640.7 | 0.04718 | 3639.0 | 0.04601 | 3637.4 |
| 610 | 0.04906 | 3664.6 | 0.04782 | 3662.9 | 0.04663 | 3661.3 |
| 620 | 0.04970 | 3688.4 | 0.04845 | 3686.8 | 0.04725 | 3685.3 |
| 630 | 0.05035 | 3712.2 | 0.04906 | 3710.7 | 0.04786 | 3709.2 |
| 640 | 0.05099 | 3736.0 | 0.04970 | 3734.5 | 0.04848 | 3733.0 |
| 650 | 0.05162 | 3759.8 | 0.05032 | 3758.4 | 0.04909 | 3756.9 |
|  | р = 8.6 MPa |  | р = 8.8 MPa |  | р = 9.0 MPa |  |
| 310 | 0.02300 | 2804.0 | 0.02219 | 2793.1 | 0.02142 | 2781.8 |
| 320 | 0.02424 | 2852.0 | 0.02344 | 2842.9 | 0.02268 | 2833.5 |
| 330 | 0.02535 | 2894.7 | 0.02456 | 2886.8 | 0.02381 | 2878.7 |
| 340 | 0.02638 | 2933.7 | 0.02559 | 2926.7 | 0.02484 | 2919.6 |
| 350 | 0.02735 | 2970.1 | 0.02655 | 2963.8 | 0.02579 | 2957.5 |
| 360 | 0.02826 | 3004.7 | 0.02746 | 2999.0 | 0.02669 | 2993.2 |
| 370 | 0.02913 | 3037.4 | 0.02832 | 3032.2 | 0.02755 | 3027.0 |
| 380 | 0.02998 | 3068.7 | 0.02915 | 3063.9 | 0.02837 | 3059.1 |
| 390 | 0.03078 | 3098.8 | 0.02995 | 3094.4 | 0.02916 | 3090.0 |
| 400 | 0.03156 | 3127.9 | 0.03072 | 3123.8 | 0.02993 | 3119.7 |
| 410 | 0.03232 | 3156.3 | 0.03148 | 3152.4 | 0.03067 | 3148.5 |
| 420 | 0.03307 | 3183.9 | 0.03221 | 3180.3 | 0.03139 | 3176.7 |
| 430 | 0.03380 | 3211.1 | 0.03293 | 3207.6 | 0.03210 | 3204.2 |
| 440 | 0.03451 | 3237.7 | 0.03364 | 3234.5 | 0.03280 | 3231.2 |
| 450 | 0.03522 | 3264.0 | 0.03433 | 3261.0 | 0.03348 | 3257.9 |
| 460 | 0.03591 | 3290.0 | 0.03501 | 3287.1 | 0.03415 | 3284.1 |
| 470 | 0.03659 | 3315.6 | 0.03568 | 3312.9 | 0.03481 | 3310.1 |
| 480 | 0.03727 | 3341.1 | 0.03635 | 3338.4 | 0.03546 | 3335.7 |
| 490 | 0.03794 | 3366.3 | 0.03700 | 3363.7 | 0.03611 | 3361.2 |
| 500 | 0.03860 | 3391.3 | 0.03765 | 3388.9 | 0.03675 | 3386.4 |
| 510 | 0.03925 | 3416.2 | 0.03829 | 3413.8 | 0.03738 | 3411.5 |
| 520 | 0.03990 | 3440.9 | 0.03893 | 3438.7 | 0.03800 | 3436.4 |
| 530 | 0.04054 | 3465.5 | 0.03955 | 3463.4 | 0.03862 | 3461.2 |
| 540 | 0.04117 | 3490.0 | 0.04018 | 3488.0 | 0.03923 | 3485.9 |
| 550 | 0.04180 | 3514.5 | 0.04080 | 3512.5 | 0.03984 | 3510.5 |
| 560 | 0.04243 | 3538.9 | 0.04141 | 3537.0 | 0.04044 | 3535.0 |
| 570 | 0.04305 | 3563.2 | 0.04202 | 3561.4 | 0.04104 | 3559.5 |
| 580 | 0.04367 | 3587.4 | 0.04263 | 3585.7 | 0.04163 | 3583.9 |
| 590 | 0.04428 | 3611.6 | 0.04323 | 3609.9 | 0.04222 | 3608.2 |
| 600 | 0.04490 | 3635.7 | 0.04383 | 3634.0 | 0.04281 | 3632.4 |
| 610 | 0.04550 | 3659.7 | 0.04443 | 3658.1 | 0.04340 | 3656.5 |
| 620 | 0.04611 | 3683.7 | 0.04502 | 3682.1 | 0.04398 | 3680.6 |
| 630 | 0.04671 | 3707.6 | 0.04561 | 3706.1 | 0.04456 | 3704.6 |
| 640 | 0.04731 | 3731.6 | 0.04620 | 3730.1 | 0.04513 | 3728.6 |
| 650 | 0.04791 | 3755.5 | 0.04678 | 3754.1 | 0.04571 | 3752.6 |
|  | р = 9.2 MPa |  | р = 9.4 MPa |  | р = 9.6 MPa |  |
| 310 | 0.02067 | 2770.1 | 0.01994 | 2757.7 | 0.01923 | 2745.0 |
| 320 | 0.02195 | 2823.8 | 0.02124 | 2813.8 | 0.02055 | 2803.6 |
| 330 | 0.02308 | 2870.5 | 0.02238 | 2862.0 | 0.02170 | 2853.4 |
| 340 | 0.02411 | 2912.4 | 0.02341 | 2905.0 | 0.02274 | 2897.5 |
| 350 | 0.02506 | 2951.0 | 0.02436 | 2944.5 | 0.02369 | 2937.9 |
| 360 | 0.02596 | 2987.4 | 0.02526 | 2981.5 | 0.02458 | 2975.5 |
| 370 | 0.02681 | 3021.7 | 0.02610 | 3016.3 | 0.02542 | 3010.9 |
| 380 | 0.02762 | 3054.3 | 0.02691 | 3049.4 | 0.02622 | 3044.4 |
| 390 | 0.02841 | 3085.5 | 0.02768 | 3080.9 | 0.02699 | 3076.4 |
| 400 | 0.02916 | 3115.5 | 0.02843 | 3111.3 | 0.02773 | 3107.1 |
| 410 | 0.02990 | 3144.6 | 0.02915 | 3140.7 | 0.02845 | 3136.8 |
| 420 | 0.03061 | 3173.0 | 0.02986 | 3169.3 | 0.02914 | 3165.6 |
| 430 | 0.03131 | 3200.8 | 0.03055 | 3197.3 | 0.02982 | 3193.8 |
| 440 | 0.03200 | 3228.0 | 0.03123 | 3224.7 | 0.03049 | 3221.4 |
| 450 | 0.03267 | 3254.8 | 0.03189 | 3251.7 | 0.03114 | 3248.5 |
| 460 | 0.03333 | 3281.2 | 0.03254 | 3278.2 | 0.03178 | 3275.3 |
| 470 | 0.03398 | 3307.3 | 0.03318 | 3304.5 | 0.03242 | 3301.6 |
| 480 | 0.03462 | 3333.1 | 0.03381 | 3330.4 | 0.03304 | 3327.7 |
| 490 | 0.03525 | 3358.6 | 0.03444 | 3356.1 | 0.03365 | 3353.5 |
| 500 | 0.03588 | 3384.0 | 0.03505 | 3381.5 | 0.03426 | 3379.1 |
| 510 | 0.03650 | 3409.2 | 0.03566 | 3406.8 | 0.03486 | 3404.5 |
| 520 | 0.03711 | 3434.2 | 0.03626 | 3431.9 | 0.03545 | 3429.7 |
| 530 | 0.03772 | 3459.0 | 0.03686 | 3456.9 | 0.03604 | 3454.7 |
| 540 | 0.03832 | 3483.8 | 0.03745 | 3481.7 | 0.03662 | 3479.6 |
| 550 | 0.03892 | 3508.5 | 0.03804 | 3506.5 | 0.03720 | 3504.4 |
| 560 | 0.03951 | 3533.1 | 0.03862 | 3531.2 | 0.03777 | 3529.2 |
| 570 | 0.04010 | 3557.6 | 0.03920 | 3555.8 | 0.03833 | 3553.9 |
| 580 | 0.04068 | 3582.1 | 0.03977 | 3580.3 | 0.03890 | 3578.5 |
| 590 | 0.04126 | 3606.4 | 0.04034 | 3604.7 | 0.03946 | 3603.0 |
| 600 | 0.04184 | 3630.7 | 0.04091 | 3629.0 | 0.04001 | 3627.3 |
| 610 | 0.04241 | 3654.9 | 0.04147 | 3653.2 | 0.04057 | 3651.6 |
| 620 | 0.04298 | 3679.0 | 0.04203 | 3677.4 | 0.04112 | 3675.9 |
| 630 | 0.04355 | 3703.1 | 0.04259 | 3701.6 | 0.04166 | 3700.0 |
| 640 | 0.04412 | 3727.1 | 0.04314 | 3725.7 | 0.04221 | 3724.2 |
| 650 | 0.04468 | 3751.2 | 0.04369 | 3749.8 | 0.04275 | 3748.3 |
|  | р = 9.8 MPa |  | р = 10.0 MPa |  | р = 10.5 MPa |  |
| 310 | 0.01853 | 2731.7 | - | - | - | - |
| 320 | 0.01989 | 2793.0 | 0.01924 | 2782.0 | 0.01771 | 2752.8 |
| 330 | 0.02105 | 2844.5 | 0.02042 | 2835.4 | 0.01893 | 2811.6 |
| 340 | 0.02209 | 2889.9 | 0.02147 | 2882.1 | 0.02000 | 2861.8 |
| 350 | 0.02304 | 2931.1 | 0.02242 | 2924.2 | 0.02095 | 2906.5 |
| 360 | 0.02393 | 2969.5 | 0.02330 | 2963.3 | 0.02184 | 2947.6 |
| 370 | 0.02477 | 3005.4 | 0.02414 | 2999.9 | 0.02266 | 2985.7 |
| 380 | 0.02556 | 3039.4 | 0.02492 | 3034.4 | 0.02344 | 3021.5 |
| 390 | 0.02632 | 3071.8 | 0.02568 | 3067.1 | 0.02418 | 3055.3 |
| 400 | 0.02705 | 3102.8 | 0.02641 | 3098.5 | 0.02489 | 3087.6 |
| 410 | 0.02776 | 3132.8 | 0.02711 | 3128.7 | 0.02558 | 3118.6 |
| 420 | 0.02845 | 3161.9 | 0.02779 | 3158.1 | 0.02624 | 3148.6 |
| 430 | 0.02912 | 3190.3 | 0.02845 | 3186.7 | 0.02689 | 3177.8 |
| 440 | 0.02978 | 3218.0 | 0.02910 | 3214.8 | 0.02752 | 3206.4 |
| 450 | 0.03043 | 3245.4 | 0.02974 | 3242.2 | 0.02814 | 3234.3 |
| 460 | 0.03106 | 3272.3 | 0.03036 | 3269.3 | 0.02874 | 3261.8 |
| 470 | 0.03168 | 3298.8 | 0.03098 | 3296.0 | 0.02933 | 3288.8 |
| 480 | 0.03230 | 3325.0 | 0.03158 | 3322.3 | 0.02992 | 3315.5 |
| 490 | 0.03290 | 3350.9 | 0.03218 | 3348.3 | 0.03049 | 3341.8 |
| 500 | 0.03350 | 3376.6 | 0.03277 | 3374.1 | 0.03106 | 3367.9 |
| 510 | 0.03409 | 3402.1 | 0.03335 | 3399.7 | 0.03162 | 3393.8 |
| 520 | 0.03467 | 3427.4 | 0.03392 | 3425.1 | 0.03217 | 3419.4 |
| 530 | 0.03525 | 3452.5 | 0.03449 | 3450.3 | 0.03272 | 3444.9 |
| 540 | 0.03582 | 3477.5 | 0.03505 | 3475.4 | 0.03326 | 3470.2 |
| 550 | 0.03639 | 3502.4 | 0.03561 | 3500.4 | 0.03380 | 3495.4 |
| 560 | 0.03695 | 3527.3 | 0.03616 | 3525.4 | 0.03433 | 3520.5 |
| 570 | 0.03751 | 3552.0 | 0.03671 | 3550.2 | 0.03486 | 3545.5 |
| 580 | 0.03806 | 3576.7 | 0.03726 | 3574.9 | 0.03538 | 3570.4 |
| 590 | 0.03861 | 3601.2 | 0.03780 | 3599.5 | 0.03590 | 3595.1 |
| 600 | 0.03916 | 3625.6 | 0.03833 | 3624.0 | 0.03641 | 3619.8 |
| 610 | 0.03397 | 3650.0 | 0.03887 | 3648.4 | 0.03692 | 3644.3 |
| 620 | 0.04024 | 3674.3 | 0.03940 | 3672.7 | 0.03743 | 3668.8 |
| 630 | 0.04078 | 3698.5 | 0.03992 | 3697.0 | 0.03794 | 3693.2 |
| 640 | 0.04131 | 3722.7 | 0.04045 | 3721.2 | 0.03844 | 3717.5 |
| 650 | 0.04184 | 3746.9 | 0.04097 | 3745.4 | 0.03894 | 3741.8 |
|  | р = 11.0 MPa |  | р = 11.5 MPa |  | р = 12.0 MPa |  |
| 320 | 0.01625 | 2720.3 | - | - | - | - |
| 330 | 0.01754 | 2785.9 | 0.01624 | 2758.1 | 0.01501 | 2727.6 |
| 340 | 0.01864 | 2840.4 | 0.01738 | 2817.7 | 0.01620 | 2793.4 |
| 350 | 0.01961 | 2888. 1 | 0.01836 | 2868.7 | 0.01721 | 2848.4 |
| 360 | 0.02049 | 2931.2 | 0.01925 | 2914.3 | 0.01810 | 2896.6 |
| 370 | 0.02131 | 2971.1 | 0.02007 | 2956.0 | 0.01893 | 2940.4 |
| 380 | 0.02208 | 3008.3 | 0.02084 | 2994.7 | 0.01969 | 2980.7 |
| 390 | 0.02281 | 3043.2 | 0.02156 | 3030.8 | 0.02040 | 3018.1 |
| 400 | 0.02351 | 3076.4 | 0.02224 | 3065.0 | 0.02108 | 3053.3 |
| 410 | 0.02418 | 3108.2 | 0.02290 | 3097.7 | 0.02173 | 3086.9 |
| 420 | 0.02483 | 3138.9 | 0.02354 | 3129.1 | 0.02235 | 3119.1 |
| 430 | 0.02546 | 3168.8 | 0.02416 | 3159.6 | 0.02296 | 3150.2 |
| 440 | 0.02607 | 3197.8 | 0.02475 | 3189.2 | 0.02354 | 3180.4 |
| 450 | 0.02667 | 3226.2 | 0.02534 | 3218.1 | 0.02411 | 3209.9 |
| 460 | 0.02726 | 3254.1 | 0.02591 | 3246.4 | 0.02467 | 3238.6 |
| 470 | 0.02784 | 3281.6 | 0.02647 | 3274.2 | 0.02521 | 3266.9 |
| 480 | 0.02840 | 3308.6 | 0.02702 | 3301.6 | 0.02575 | 3294.6 |
| 490 | 0.02896 | 3335.3 | 0.02756 | 3328.6 | 0.02627 | 3322.0 |
| 500 | 0.02951 | 3361.6 | 0.02809 | 3355.3 | 0.02679 | 3349.0 |
| 510 | 0.03005 | 3387.8 | 0.02861 | 3381.7 | 0.02730 | 3375.6 |
| 520 | 0.03058 | 3413.7 | 0.02913 | 3407.9 | 0.02780 | 3402.1 |
| 530 | 0.03111 | 3439.4 | 0.02964 | 3433.8 | 0.02829 | 3428.2 |
| 540 | 0.03163 | 3464.9 | 0.03014 | 3459.6 | 0.02878 | 3454.2 |
| 550 | 0.03215 | 3490.3 | 0.03064 | 3485.2 | 0.02926 | 3480.0 |
| 560 | 0.03266 | 3515.6 | 0.03114 | 3510.7 | 0.02974 | 3505.7 |
| 570 | 0.03317 | 3540.8 | 0.03163 | 3536.0 | 0.03022 | 3531.3 |
| 580 | 0.03367 | 3565.8 | 0.03211 | 3561.3 | 0.03068 | 3556.7 |
| 590 | 0.03417 | 3590.7 | 0.03260 | 3586.3 | 0.03115 | 3581.9 |
| 600 | 0.03467 | 3615.5 | 0.03307 | 3611.3 | 0.03161 | 3607.0 |
| 610 | 0.03516 | 3640.2 | 0.03355 | 3636.1 | 0.03207 | 3632.0 |
| 620 | 0.03565 | 3664.8 | 0.03402 | 3660.8 | 0.03252 | 3656.9 |
| 630 | 0.03614 | 3689.3 | 0.03449 | 3685.5 | 0.03298 | 3681.6 |
| 640 | 0.03662 | 3713.8 | 0.03495 | 3710.1 | 0.03343 | 3706.4 |
| 650 | 0.03710 | 3738.2 | 0.03542 | 3734.6 | 0.03387 | 3731.0 |
|  | р = 12.5 MPa |  | р = 13.0 MPa |  | р = 13.5 MPa |  |
| 330 | 0.01382 | 2693.4 | - | - | - | - |
| 340 | 0.01508 | 2767.2 | 0.01402 | 2738.8 | 0.01300 | 2707.6 |
| 350 | 0.01613 | 2826.8 | 0.01511 | 2804.0 | 0.01415 | 2779.7 |
| 360 | 0.01704 | 2878.2 | 0.01604 | 2858.9 | 0.01511 | 2838.7 |
| 370 | 0.01786 | 2924.3 | 0.01688 | 2907.5 | 0.01595 | 2890 1 |
| 380 | 0.01862 | 2966.2 | 0.01764 | 2951.4 | 0.01672 | 2936.0 |
| 390 | 0.01933 | 3005.0 | 0.01834 | 2991.7 | 0.01742 | 2977.9 |
| 400 | 0.02001 | 3041.4 | 0.01901 | 3029.3 | 0.01808 | 3016.8 |
| 410 | 0.02065 | 3075.9 | 0.01964 | 3064.8 | 0.01871 | 3053.4 |
| 420 | 0.02126 | 3109.0 | 0.02025 | 3098.6 | 0.01931 | 3088.1 |
| 430 | 0.02185 | 3140.8 | 0.02083 | 3131.1 | 0.01988 | 3121.4 |
| 440 | 0.02243 | 3171.5 | 0.02139 | 3162.6 | 0.02044 | 3153.4 |
| 450 | 0.02298 | 3201.5 | 0.02194 | 3193.1 | 0.02097 | 3184.5 |
| 460 | 0.02353 | 3230.8 | 0.02247 | 3222.8 | 0.02149 | 3214.7 |
| 470 | 0.02406 | 3259.4 | 0.02299 | 3251.9 | 0.02200 | 3244.3 |
| 480 | 0.02458 | 3287.5 | 0.02350 | 3280.4 | 0.02250 | 3273.2 |
| 490 | 0.02509 | 3315.2 | 0.02400 | 3308.5 | 0.02298 | 3301.6 |
| 500 | 0.02559 | 3342.6 | 0.02448 | 3336.1 | 0.02346 | 3329.6 |
| 510 | 0.02608 | 3369.5 | 0.02496 | 3363.4 | 0.02393 | 3357.2 |
| 520 | 0.02657 | 3396.2 | 0.02544 | 3390.3 | 0.02439 | 3384.4 |
| 530 | 0.02705 | 3422.6 | 0.02590 | 3417.0 | 0.02484 | 3411.3 |
| 540 | 0.02752 | 3448.8 | 0.02637 | 3443.4 | 0.02529 | 3438.0 |
| 550 | 0.02799 | 3474.9 | 0.02682 | 3469.7 | 0.02574 | 3464.5 |
| 560 | 0.02846 | 3500.8 | 0.02727 | 3495.8 | 0.02617 | 3490.8 |
| 570 | 0.02892 | 3526.5 | 0.02772 | 3521.7 | 0.02661 | 3516.9 |
| 580 | 0.02937 | 3552.1 | 0.02816 | 3547.5 | 0.02703 | 3542.8 |
| 590 | 0.02982 | 3577.5 | 0.02859 | 3573.0 | 0.02746 | 3568.6 |
| 600 | 0.03027 | 3602.7 | 0.02903 | 3598.4 | 0.02788 | 3594.2 |
| 610 | 0.03071 | 3627.9 | 0.02946 | 3623.7 | 0.02829 | 3619.6 |
| 620 | 0.03115 | 3652.9 | 0.02988 | 3648.9 | 0.02871 | 3644.9 |
| 630 | 0.03159 | 3677.8 | 0.03030 | 3673.9 | 0.02912 | 3670.0 |
| 640 | 0.03202 | 3702.6 | 0.03072 | 3698.9 | 0.02952 | 3695.1 |
| 650 | 0.03245 | 3727.4 | 0.03114 | 3723.8 | 0.02993 | 3720.1 |
|  | р = 14.0 MPa |  | р = 14.5 MPa |  | р= 15.0 MPa |  |
| 340 | 0.01201 | 2672.6 | 0.01101 | 2632.3 | - | - |
| 350 | 0.01323 | 2753.5 | 0.01235 | 2725.1 | 0.01148 | 2693.8 |
| 360 | 0.01422 | 2817.4 | 0.01338 | 2794.9 | 0.01258 | 2771.3 |
| 370 | 0.01508 | 2871.9 | 0.01426 | 2853.0 | 0.01349 | 2833.3 |
| 380 | 0.01585 | 2920.2 | 0.01504 | 2903.7 | 0.01428 | 2886.7 |
| 390 | 0.01656 | 2963.8 | 0.01575 | 2949.3 | 0.01500 | 2934.3 |
| 400 | 0.01722 | 3004.0 | 0.01641 | 2991.0 | 0.01566 | 2977.6 |
| 410 | 0.01784 | 3041.7 | 0.01703 | 3029.8 | 0.01627 | 3017.7 |
| 420 | 0.01844 | 3077.4 | 0.01762 | 3066.4 | 0.01685 | 3055.3 |
| 430 | 0.01900 | 3111.4 | 0.01818 | 3101.3 | 0.01741 | 3091.1 |
| 440 | 0.01954 | 3144.2 | 0.01872 | 3134.8 | 0.01794 | 3125.2 |
| 450 | 0.02007 | 3175.8 | 0.01923 | 3167.0 | 0.01845 | 3158.2 |
| 460 | 0.02058 | 3206.6 | 0.01974 | 3198.3 | 0.01894 | 3190.0 |
| 470 | 0.02108 | 3236.6 | 0.02022 | 3228.8 | 0.01942 | 3221.0 |
| 480 | 0.02157 | 3265.9 | 0.02070 | 3258.6 | 0.01989 | 3251.2 |
| 490 | 0.02204 | 3294.7 | 0.02117 | 3287.8 | 0.02035 | 3280.7 |
| 500 | 0.02251 | 3323.0 | 0.02162 | 3316.4 | 0.02079 | 3309.7 |
| 510 | 0.02297 | 3350.9 | 0.02207 | 3344.6 | 0.02123 | 3338.3 |
| 520 | 0.02342 | 3378.4 | 0.02251 | 3372.5 | 0.02166 | 3366.4 |
| 530 | 0.02386 | 3405.6 | 0.02294 | 3399.9 | 0.02206 | 3394.1 |
| 540 | 0.02430 | 3432.5 | 0.02337 | 3427.0 | 0.02250 | 3421.5 |
| 550 | 0.02473 | 3459.2 | 0.02379 | 3454.0 | 0.02291 | 3448.7 |
| 560 | 0.02515 | 3485.8 | 0.02420 | 3480.7 | 0.02332 | 3475.6 |
| 570 | 0.02557 | 3512.1 | 0.02461 | 3507.2 | 0.02372 | 3502.3 |
| 580 | 0.02599 | 3538.2 | 0.02502 | 3533.5 | 0.02411 | 3528.8 |
| 590 | 0.02640 | 3564.1 | 0.02542 | 3559.6 | 0.02450 | 3555.1 |
| 600 | 0.02681 | 3589.8 | 0.02582 | 3585.5 | 0.02489 | 3581.2 |
| 610 | 0.02722 | 3615.4 | 0.02621 | 3611.2 | 0.02527 | 3607.0 |
| 620 | 0.02762 | 3640.8 | 0.02660 | 3636.8 | 0.02565 | 3632.8 |
| 630 | 0.02801 | 3666.1 | 0.02699 | 3662.2 | 0.02603 | 3658.3 |
| 640 | 0.02841 | 3691.3 | 0.02737 | 3687.6 | 0.02640 | 3683.8 |
| 650 | 0.02880 | 3716.5 | 0.02775 | 3712.8 | 0.02677 | 3709.1 |
|  | р = 15.5 MPa |  | р = 16.0 MPa |  | р = 16.5 MPa |  |
| 350 | 0.01064 | 2658.8 | 0.00978 | 2618.5 | 0.00889 | 2570.1 |
| 360 | 0.01181 | 2745.6 | 0.01107 | 2717.8 | 0.01034 | 2687.4 |
| 370 | 0.01275 | 2812.4 | 0.01205 | 2790.5 | 0.01137 | 2767.2 |
| 380 | 0.01356 | 2869.0 | 0.01286 | 2850.6 | 0.01222 | 2831.3 |
| 390 | 0.01428 | 2918.8 | 0.01360 | 2902.9 | 0.01296 | 2886.4 |
| 400 | 0.01494 | 2963.8 | 0.01427 | 2949.7 | 0.01363 | 2935.2 |
| 410 | 0.01556 | 3005.2 | 0.01488 | 2992.5 | 0.01425 | 2979.6 |
| 420 | 0.01614 | 3044.0 | 0.01546 | 3032.5 | 0.01482 | 3020.7 |
| 430 | 0.01668 | 3080.6 | 0.01600 | 3070.0 | 0.01536 | 3059.2 |
| 440 | 0.01721 | 3115.6 | 0.01652 | 3105.8 | 0.01588 | 3095.8 |
| 450 | 0.01771 | 3149.2 | 0.01702 | 3140.0 | 0.01637 | 3130.8 |
| 460 | 0.01820 | 3181.6 | 0.01750 | 3173.0 | 0.01685 | 3164.4 |
| 470 | 0.01867 | 3213.0 | 0.01797 | 3205.0 | 0.01731 | 3196.9 |
| 480 | 0.01913 | 3243.7 | 0.01842 | 3236.2 | 0.01775 | 3228.5 |
| 490 | 0.01958 | 3273.7 | 0.01886 | 3266.5 | 0.01819 | 3259.3 |
| 500 | 0.02002 | 3303.0 | 0.01929 | 3296.3 | 0.01861 | 3289.5 |
| 510 | 0.02045 | 3331.9 | 0.01971 | 3325.4 | 0.01902 | 3319.0 |
| 520 | 0.02087 | 3360.3 | 0.02013 | 3354.2 | 0.01943 | 3348.0 |
| 530 | 0.02128 | 3388.3 | 0.02053 | 3382.4 | 0.01982 | 3376.6 |
| 540 | 0.02169 | 3416.0 | 0.02093 | 3410.4 | 0.02021 | 3404.8 |
| 550 | 0.02209 | 3443.4 | 0.02132 | 3438.0 | 0.02060 | 3432.6 |
| 560 | 0.02249 | 3470.5 | 0.02171 | 3465.4 | 0.02098 | 3460.2 |
| 570 | 0.02288 | 3497.4 | 0.02209 | 3492.5 | 0.02135 | 3487.6 |
| 580 | 0.02326 | 3524.1 | 0.02247 | 3519.4 | 0.02172 | 3514.6 |
| 590 | 0.02364 | 3550.6 | 0.02284 | 3546.0 | 0.02208 | 3541.5 |
| 600 | 0.02402 | 3576.8 | 0.02321 | 3572.4 | 0.02244 | 3568.0 |
| 610 | 0.02440 | 3602.8 | 0.02357 | 3598.6 | 0.02280 | 3594.4 |
| 620 | 0.02477 | 3628.7 | 0.02393 | 3624.6 | 0.02315 | 3620.6 |
| 630 | 0.02513 | 3654.4 | 0.02429 | 3650.5 | 0.02350 | 3646.5 |
| 640 | 0.02550 | 3680.0 | 0.02465 | 3676.2 | 0.02385 | 3672.4 |
| 650 | 0.02586 | 3705.5 | 0.02500 | 3701.8 | 0.02419 | 3698.1 |
|  | р = 17.0 MPa |  | р = 17.5 MPa |  | р = 18.0 MPa |  |
| 360 | 0.00962 | 2653.6 | 0.00889 | 2615.2 | 0.00814 | 2569.8 |
| 370 | 0.01072 | 2742.3 | 0.01008 | 2715.7 | 0.00946 | 2686.8 |
| 380 | 0.01160 | 2811.2 | 0.01100 | 2790.1 | 0.01042 | 2767.8 |
| 390 | 0.01235 | 2869.3 | 0.01177 | 2851.5 | 0.01122 | 2833.1 |
| 400 | 0.01303 | 2920.2 | 0.01246 | 2904.9 | 0.01191 | 2889.0 |
| 410 | 0.01365 | 2966.3 | 0.01308 | 2952.6 | 0.01254 | 2938.7 |
| 420 | 0.01422 | 3008.6 | 0.01365 | 2996.4 | 0.01311 | 2983.9 |
| 430 | 0.01476 | 3048.3 | 0.01419 | 3037.1 | 0.01365 | 3025.7 |
| 440 | 0.01527 | 3085.7 | 0.01470 | 3075.4 | 0.01415 | 3065.0 |
| 450 | 0.01576 | 3121.4 | 0.01518 | 3111.9 | 0.01463 | 3102.3 |
| 460 | 0.01623 | 3155.7 | 0.01565 | 3146.8 | 0.01509 | 3137.9 |
| 470 | 0.01668 | 3188.8 | 0.01610 | 3180.5 | 0.01554 | 3172.1 |
| 480 | 0.01712 | 3220.8 | 0.01653 | 3213.1 | 0.01597 | 3205.2 |
| 490 | 0.01755 | 3252.1 | 0.01695 | 3244.7 | 0.01638 | 3237.3 |
| 500 | 0.01797 | 3282.6 | 0.01736 | 3275.7 | 0.01678 | 3268.7 |
| 510 | 0.01837 | 3312.4 | 0.01776 | 3305.9 | 0.01718 | 3299.3 |
| 520 | 0.01877 | 3341.8 | 0.01815 | 3335.5 | 0.01756 | 3329.3 |
| 530 | 0.01916 | 3370.6 | 0.01853 | 3364.7 | 0.01794 | 3358.7 |
| 540 | 0.01954 | 3399.1 | 0.01891 | 3393.4 | 0.01831 | 3387.7 |
| 550 | 0.01992 | 3427.2 | 0.01928 | 3421.8 | 0.01867 | 3416.4 |
| 560 | 0.02029 | 3455.1 | 0.01964 | 3449.8 | 0.01903 | 3444.7 |
| 570 | 0.02066 | 3482.6 | 0.02000 | 3477.6 | 0.01938 | 3472.6 |
| 580 | 0.02102 | 3509.9 | 0.02035 | 3505.1 | 0.01973 | 3500.3 |
| 590 | 0.02137 | 3536.9 | 0.02070 | 3532.3 | 0.02007 | 3527.7 |
| 600 | 0.02173 | 3563.6 | 0.02105 | 3559.2 | 0.02041 | 3554.8 |
| 610 | 0.02207 | 3590.2 | 0.02139 | 3585.9 | 0.02074 | 3581.6 |
| 620 | 0.02242 | 3616.5 | 0.02172 | 3612.4 | 0.02107 | 3608.2 |
| 630 | 0.02276 | 3642.6 | 0.02206 | 3638.6 | 0.02140 | 3634.9 |
| 640 | 0.02310 | 3668.6 | 0.02239 | 3664.8 | 0.02172 | 3660.9 |
| 650 | 0.02343 | 3694.4 | 0.02272 | 3690.7 | 0.02204 | 3687.0 |
|  | р = 18.5 MPa |  | р = 19.0 MPa |  | р = 19.5 MPa |  |
| 360 | 0.00730 | 2511.7 | - | - | - | - |
| 370 | 0.00885 | 2655.1 | 0.00824 | 2619.8 | 0.00761 | 2579.4 |
| 380 | 0.00987 | 2744.2 | 0.00933 | 2719.1 | 0.00880 | 2692.3 |
| 390 | 0.01068 | 2813.9 | 0.01017 | 2793.9 | 0.00968 | 2772.9 |
| 400 | 0.01139 | 2872.7 | 0.01089 | 2855.7 | 0.01041 | 2838.2 |
| 410 | 0.01202 | 2924.3 | 0.01153 | 2909.5 | 0.01106 | 2894.5 |
| 420 | 0.01260 | 2971.1 | 0.01211 | 2958.0 | 0.01164 | 2944.6 |
| 430 | 0.01313 | 3014.2 | 0.01264 | 3002.4 | 0.01218 | 2990.4 |
| 440 | 0.01364 | 3054.4 | 0.01314 | 3043.7 | 0.01268 | 3032.8 |
| 450 | 0.01411 | 3092.5 | 0.01362 | 3082.6 | 0.01315 | 3072.6 |
| 460 | 0.01457 | 3128.8 | 0.01407 | 3119.7 | 0.01360 | 3110.4 |
| 470 | 0.01501 | 3163.7 | 0.01451 | 3155.1 | 0.01403 | 3146.5 |
| 480 | 0.01543 | 3197.3 | 0.01493 | 3189.3 | 0.01445 | 3181.2 |
| 490 | 0.01584 | 3229.9 | 0.01533 | 3222.4 | 0.01485 | 3214.8 |
| 500 | 0.01624 | 3261.7 | 0.01573 | 3254.5 | 0.01524 | 3247.7 |
| 510 | 0.01663 | 3292.6 | 0.01611 | 3285.9 | 0.01561 | 3279.1 |
| 520 | 0.01701 | 3322.9 | 0.01648 | 3316.6 | 0.01598 | 3310.2 |
| 530 | 0.01738 | 3352.7 | 0.01685 | 3346.7 | 0.01634 | 3340.6 |
| 540 | 0.01774 | 3382.0 | 0.01720 | 3376.2 | 0.01669 | 3370.4 |
| 550 | 0.01811 | 3410.9 | 0.01756 | 3405.4 | 0.01704 | 3399.9 |
| 560 | 0.01845 | 3439.4 | 0.01790 | 3434.2 | 0.01738 | 3428.9 |
| 570 | 0.01880 | 3467.6 | 0.01824 | 3462.6 | 0.01771 | 3457.5 |
| 580 | 0.01914 | 3495.5 | 0.01857 | 3490.6 | 0.01804 | 3485.8 |
| 590 | 0.01947 | 3523.0 | 0.01890 | 3518.4 | 0.01836 | 3513.8 |
| 600 | 0.01980 | 3550.3 | 0.01923 | 3545.9 | 0.01868 | 3541.4 |
| 610 | 0.02013 | 3577.4 | 0.01955 | 3573.1 | 0.01900 | 3568.8 |
| 620 | 0.02045 | 3604.1 | 0.01986 | 3600.0 | 0.01931 | 3595.8 |
| 630 | 0.02077 | 3630.7 | 0.02018 | 3626.7 | 0.01962 | 3622.7 |
| 640 | 0.02109 | 3657.1 | 0.02049 | 3653.2 | 0.01992 | 3649.4 |
| 650 | 0.02140 | 3683.3 | 0.02080 | 3679.6 | 0.02022 | 3675.9 |

TABLE OF CONTENTS

PREFACE	3

1. GENERAL STATEMENTS	8

2. HEAT-TRANSFER CALCULATIONS	10

2.1. Basic Equations.	10

2.2. Overall Heat Transfer Coefficient	11

2.3. Reduced Heat Transfer Coefficient h1rdc	13

2.4. Convective Heat Transfer Coefficient (hc)	16

2.5. Heat Transfer Coefficient from Wall to Internal Medium (h2)	33

2.6. Contamination Factor and Thermal Efficiency	35

2.7. Average Temperature Difference	39

3. CALCULATION OF AERODYNAMIC RESISTANCE	48

3.1.The aerodynamic resistance of the bundles of finned tubes in crossflow	48

4. CALCULATION OF HYDRAULIC RESISTANCE	64

4.1. Hydraulic calculation of the tube elements	64

4.2. Total hydraulic resistance of the tube element	65

4.3. Hydraulic friction resistance and local resistances of the heat transfer surfaces,	66

4.4. Friction Resistance	66

4.5. The local resistances in the tube elements	71

4.6. Pressure Variation in Collectors [9]	76

5. CALCULATION OF TEMPERATURE MODE OF FINNED TUBES	82

5.1. Order to evaluate the reliability and perform the strength design for transversely finned tubes	82

5.2. Temperature of the fin base	82

5.3. Temperature at Fin Tip	99

5.4. Mean Integral Temperature of Fin	100

5.5. Temperature of the Inside Surface of Tube	100

5.6. Thickness-average temperature of the tube wall	100

6. STRENGTH DESIGN [12]	102

6.1. Strength design of heat transfer surfaces	102

6.2. Design Pressure	102

6.3. Design Temperature	102

6.5. Calculation of Allowable Wall Thickness of Finning-Carrying Tube	104

7. EXAMPLES OF CALCULATIONS	111

7.1. Calculation Assignment	111

7.2. Heat Balance	111

7.3. Structural Features of WAHE	113

7.4. Calculation of Area of Heat-Transfer Surface	120

7.5. Calculation of Aerodynamic Resistance	128

7.6. Calculation of Hydraulic Resistance of WAHE	130

REFERENCES	143

APPEDICES	145

APPENDIX A: UNITS CONVERSION	146

APPENDIX B: RECOMMENDED THERMOPHYSICAL PROPERTIES SOFTWARE FOR GASES AND LIQUIDS	152

APPENDIX C: TABLES OF PROPERTIES OF SUBSTANCES	154